{"text_format":"2","workbook":"xlsx","n_sheets":6,"sheets":["CC中央供冷系统 ","CH中央供热系统","AT空调末端系统","VT通风系统","KL厨房排油烟系统","AD空调人防系统"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"CC中央供冷系统 ","index":0,"n_rows":84,"n_cols":10,"rows_kept":84,"cut":false,"hidden":false,"merged":[[77,0,82,1],[83,0,83,1],[0,0,0,9],[1,0,1,1],[2,0,33,1],[34,0,76,0],[34,1,64,1],[65,1,71,1],[72,1,76,1]]}
["中央供冷系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"冷源类型","CoolSourceType",null,"Enum","S","D1","1. 离心式制冷机 2. 螺杆式制冷机 3. 吸收式制冷机 4. 空气源热泵 5. 水源热泵 6. 地源热泵 7. 多联机 8. 分体机 8. 热电冷三联供机组 99. 其他"]
[null,null,"最大供冷能力","MaxCoolP","kW","Num","M","A2"]
[null,null,"最小供冷能力","MinCoolP","kW","Num","R","A2"]
[null,null,"供冷性质","CoolType",null,"Enum","S","D1","1. 超低温供冷 2. 低温供冷 3. 高温供冷 99. 其他"]
[null,null,"冷冻泵形式","ChillPumpType",null,"Enum","S","D1","1. 一次泵系统 2. 二次泵系统 99. 其他"]
[null,null,"（一次）冷冻泵台数","PrimaryChillPumpNum","台","Num","M","A2"]
[null,null,"（一次）冷冻泵备用台数","BackupPrimaryChillPumpNum","台","Num","M","A2"]
[null,null,"二次冷冻泵台数","SecondaryChillPumpNum","台","Num","M","A2"]
[null,null,"二次冷冻泵备用台数","BackupSecondaryChillPumpNum","台","Num","M","A2"]
[null,null,"冷冻泵变频类型","ChillPumpFreqTransType",null,"Enum","S","D1","1. 定频 2. 档位 3. 变频 99. 其他"]
[null,null,"冷冻泵与冷机连接形式","ChillPumpChillerConnectType",null,"Enum","M","D1","1. 一机对一泵 2. 分别并联 99. 其他"]
[null,null,"冷冻水管道定压方式","ChillWaterConstantPressType",null,"Enum","R","D1","1. 膨胀水箱定压 2. 补水泵定压 3. 旁通管定压  99. 其他"]
[null,null,"额定定压点压强","RatedConstantPress","MPa","Num","R","A2"]
[null,null,"分水器出口支路数","DistributorBrNum","支","Num","M","A2"]
[null,null,"集水器入口支路数","CollectorBrNum","支","Num","M","A2"]
[null,null,"分集水器间是否旁通","isDistributorCollectorBypass",null,"Bool","M","E1","0. 无旁通 1. 有旁通"]
[null,null,"冷却塔台数","CoolTowerNum","台","Num","M","A2"]
[null,null,"冷却泵台数","CoolPumpNum","台","Num","M","A2"]
[null,null,"冷却泵备用台数","BackupCoolPumpNum","台","Num","M","A2"]
[null,null,"冷却泵变频类型","CoolPumpFreqTransType",null,"Enum","S","D1","1. 定频 2. 档位 3. 变频 99. 其他"]
[null,null,"冷却泵与冷却塔连接形式","CoolPumpCoolTowerConnectType",null,"Enum","M","D1","1. 一塔对一泵 2. 分别并联 99. 其他"]
[null,null,"有无蓄冷设备","isCoolStore",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"蓄冷容量","CoolStoreCap","kWh","Num","M","A2"]
[null,null,"最大蓄冷功率","MaxCoolStoreP","kW","Num","R","A2"]
[null,null,"最大释冷功率","MaxCoolReleaseP","kW","Num","R","A2"]
[null,null,"蓄冷温度","RatedCoolStoreTemp","℃","Num","R","A2"]
[null,null,"额定冷冻水供水温度","RatedChillWaterSupplyTemp","℃","Num","S","A2"]
[null,null,"额定冷冻水回水温度","RatedChillWaterReturnTemp","℃","Num","M","A2"]
[null,null,"额定冷冻水总流量","RatedChillWaterFlow","m3/h","Num","M","A2"]
[null,null,"额定冷却水供水温度","RatedCoolWaterSupplyTemp","℃","Num","M","A2"]
[null,null,"额定冷却水回水温度","RatedCoolWaterReturnTemp","℃","Num","M","A2"]
[null,null,"额定冷却水总流量","RatedCoolWaterFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","S","M"]
[null,null,"耗热功率","SysHeatConsumP","kW","Inst","M","M",null,"吸收式制冷机"]
[null,null,"逐时供冷量","CoolP","kW","Inst","M","M"]
[null,null,"逐时供热量","HeatP","kW","Inst","M","M",null,"吸收式或热电冷联供系统"]
[null,null,"冷机开启台数","ChillerRunNum","台","Inst","S","M"]
[null,null,"冷机工作频率","ChillerFreq","Hz","Inst","R","L"]
[null,null,"冷冻泵开启台数","ChillPumpRunNum","台","Inst","S","M"]
[null,null,"冷冻泵运行频率","ChillPumpFreq","Hz","Inst","M","L"]
[null,null,"冷却泵开启台数","CoolPumpRunNum","台","Inst","S","M"]
[null,null,"冷却泵运行频率","CoolPumpFreq","Hz","Inst","M","L"]
[null,null,"冷却塔开启台数","CoolTowerRunNum","台","Inst","S","M"]
[null,null,"冷却塔运行频率","CoolTowerFreq","Hz","Inst","M","L"]
[null,null,"冷冻水供水干管温度","ChillWaterMainSupplyTemp","℃","Inst","S","L",null,"分水器"]
[null,null,"冷冻水供水干管压力","ChillWaterMainSupplyPress","MPa","Inst","M","L",null,"分水器"]
[null,null,"冷冻水回水干管温度","ChillWaterMainReturnTemp","℃","Inst","S","L",null,"集水器"]
[null,null,"冷冻水回水干管压力","ChillWaterMainReturnPress","MPa","Inst","M","L",null,"集水器"]
[null,null,"冷冻水总流量","ChillWaterFlow","m3/h","Inst","S","L"]
[null,null,"分集水器旁通阀开度","DistributorCollectorBypassOpening","%","Inst","M","L"]
[null,null,"分集水器旁通管流量","DistributorCollectorBypassFlow","m3/h","Inst","R","L"]
[null,null,"冷却水供水干管温度","CoolWaterMainSupplyTemp","℃","Inst","S","L"]
[null,null,"冷却水供水干管压力","CoolWaterMainSupplyPress","MPa","Inst","M","L"]
[null,null,"冷却水回水干管温度","CoolWaterMainReturnTemp","℃","Inst","S","L"]
[null,null,"冷却水回水干管压力","CoolWaterMainReturnPress","MPa","Inst","M","L"]
[null,null,"冷却水总流量","CoolWaterFlow","m3/h","Inst","S","L"]
[null,null,"逐时蓄冷功率","CoolStoreP","kW","Inst","M","M"]
[null,null,"逐时释冷功率","CoolReleaseP","kW","Inst","M","M"]
[null,null,"蓄冷量","CoolStore","kWh","Inst","R","M"]
[null,"瞬时指标","冷机组负载率","ChillersPLR","%","Inst","R","M"]
[null,null,"冷机组COP","ChillersCOP",null,"Inst","R","M"]
[null,null,"冷冻水输配系数","WTFch",null,"Inst","R","M"]
[null,null,"冷却水输配系数","WTFc",null,"Inst","R","M"]
[null,null,"分集水器压差","DistributorCollectorDetaPress","MPa","Inst","R","M"]
[null,null,"蓄冷效率","CoolStoreEff","%","Inst","R","M"]
[null,null,"系统COP","SysCOP",null,"Inst","M","M"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计耗热量","AccHeatConsum","kWh","Acc","R","M",null,"吸收式制冷机"]
[null,null,"累计供冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计供热量","AccHeat","kWh","Acc","M","M",null,"吸收式或热电冷联供系统"]
[null,null,"系统IPLV","SysIPLV",null,"Inst","R","M"]
["设定参数",null,"冷冻水供水温度设定","ChillWaterOutTempSet","℃","Nump","S","L"]
[null,null,"冷冻水温差设定","ChillWaterDetaTempSet","℃","Nump","S","L"]
[null,null,"冷冻水压差设定","ChillWaterDetaPressSet","MPa","Nump","S","L"]
[null,null,"冷却水供水温度设定","CoolWaterOutTempSet","℃","Nump","S","L"]
[null,null,"冷却水温差设定","CoolWaterDetaTempSet","℃","Nump","S","L"]
[null,null,"冷却水压差设定","CoolWaterDetaPressSet","MPa","Nump","S","L"]
["报警消息"]

{"sheet":"CH中央供热系统","index":1,"n_rows":59,"n_cols":13,"rows_kept":59,"cut":false,"hidden":false,"merged":[[55,0,55,1],[56,0,56,1],[0,0,0,9],[1,0,1,1],[2,0,24,1],[25,0,54,0],[25,1,44,1],[45,1,48,1],[49,1,54,1]]}
["中央供热系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"热源类型","HeatSoureType",null,"Enum","S","D1","1. 市政热水 2. 燃煤锅炉 3. 燃油锅炉 4. 燃气锅炉 5. 电锅炉 6. 空气源热泵 7. 水源热泵 8. 地源热泵 9. 分散采暖设备 99. 其他"]
[null,null,"热媒类型","HeatMediumType",null,"Enum","S","D1","1. 蒸汽 2. 热水 99. 其他"]
[null,null,"与市政管网连接方式","MunicipalConnectType",null,"Bool","S","E1","0. 直连 1. 间连 "]
[null,null,"系统循环形式","SysCycleType",null,"Enum","M","D1","1. 重力循环 2. 机械循环 99. 其他"]
[null,null,"系统管道形式","SysPipeType",null,"Enum","R","D1","1. 单管串联 2. 单管跨越 3. 双管同程式 4. 双管异程式 99. 其他"]
[null,null,"热水管道定压方式","HeatWaterConstantPressType",null,"Enum","R","D1","1. 膨胀水箱定压 2. 补水泵定压 3. 旁通管定压  99. 其他"]
[null,null,"定压点压强","ConstantPress","MPa","Num","R","A2"]
[null,null,"分水器出口支路数","DistributorBrNum","支","Num","M","A2"]
[null,null,"集水器入口支路数","CollectorBrNum","支","Num","M","A2"]
[null,null,"分集水器间是否旁通","isDistributorCollectorBypass",null,"Bool","M","E1","0. 无旁通 1. 有旁通"]
[null,null,"供回水方式","SupplyReturnWaterType",null,"Enum","R","D1","1. 上供上回 2. 上供下回 3. 下供上回 4. 下供下回 99. 其他"]
[null,null,"热计量方式","HeatMeterType",null,"Enum","R","D1","1. 热量表法 2. 散热器热分配法 3. 流温法 4. 通断时间面积法 5. 温度法 99. 其他"]
[null,null,"循环泵台数","HeatPumpNum","台","Num","M","A2"]
[null,null,"循环泵备用台数","BackupHeatPumpNum","台","Num","M","A2"]
[null,null,"循环泵是否变频","isHeatPumpFreqTrans",null,"Enum","S","D1","1. 定频 2. 档位 3. 变频 99. 其他"]
[null,null,"循环泵与热源连接形式","HeatPumpHeaterConnectType",null,"Enum","M","D1","1. 一机对一泵 2. 分别并联 99. 其他"]
[null,null,"额定供水温度","RatedHeatWaterSupplyTemp","℃","Num","S","A2",null,"热水系统"]
[null,null,"额定供蒸汽压力","RatedVaporSupplyPress","MPa","Num","S","A2",null,"蒸汽系统"]
[null,null,"额定回水温度","RatedHeatWaterReturnTemp","℃","Num","M","A2"]
[null,null,"额定循环流量","RatedHeatWaterFlow","m3/h","Num","M","A2"]
[null,null,"入户方式","IndoorType",null,"Enum","R","D1","1. 垂直 2. 水平 99. 其他"]
[null,null,"散热设备","RadiationType",null,"Enum","M","D1","1. 暖气片 2. 地板辐射 3. 暖风机 99. 其他","不与空调末端共用时"]
[null,null,"最不利环路压降","WorstLoopPressDrop","MPa","Num","M","A2",null,"设计工况"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"耗煤量","CoalConsumP","t/h","Inst","M","M"]
[null,null,"耗油量","FuelConsumP","L/h","Inst","M","M"]
[null,null,"耗气量","GasConsumP","m3/h","Inst","M","M"]
[null,null,"逐时供热量","HeatP","kW","Inst","M","M"]
[null,null,"热源开启台数","HeaterRunNum","台","Inst","S","M"]
[null,null,"热源运行频率","HeaterFreq","Hz","Inst","R","L"]
[null,null,"循环泵开启台数","HeatPumpRunNum","台","Inst","S","M"]
[null,null,"循环泵运行频率","HeatPumpFreq ","Hz","Inst","R","L"]
[null,null,"供水干管温度","HeatWaterMainSupplyTemp","℃","Inst","S","L",null,"分水器"]
[null,null,"供水干管压力","HeatWaterMainSupplyPress","MPa","Inst","S","L",null,"分水器"]
[null,null,"供蒸汽压力","VaporMainSupplyPress","MPa","Inst","S","L",null,"分汽器"]
[null,null,"回水干管温度","HeatWaterMainReturnTemp","℃","Inst","S","L",null,"集水器"]
[null,null,"回水干管压力","HeatWaterMainReturnPress","MPa","Inst","S","L",null,"集水器"]
[null,null,"循环流量","HeatWaterFlow","m3/h","Inst","S","L"]
[null,null,"旁通管流量","BypassFlow","m3/h","Inst","R","L"]
[null,"瞬时指标","热源COP（效率）","HeatersCOP",null,"Inst","R","M"]
[null,null,"热水输配系数","WTFht",null,"Inst","R","M"]
[null,null,"分集水器压差","DistributorCollectorDetaPress","MPa","Inst","R","M"]
[null,null,"系统COP","SysCOP",null,"Inst","R","M"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计耗煤量","AccCoalConsum","t","Acc","M","M"]
[null,null,"累计耗油量","AccFuelConsum","L","Acc","M","M"]
[null,null,"累计耗气量","AccGasConsum","m3","Acc","M","M"]
[null,null,"累计供热量","AccHeat ","kWh","Acc","M","M"]
[null,null,"IPLV","SysIPLV",null,"Inst","R","M"]
["设定参数"]
["报警消息"]
[]
[{"$nulls":12},"          "]

{"sheet":"AT空调末端系统","index":2,"n_rows":33,"n_cols":10,"rows_kept":33,"cut":false,"hidden":false,"merged":[[31,0,31,1],[32,0,32,1],[0,0,0,9],[1,0,1,1],[2,0,8,1],[9,0,30,0],[9,1,20,1],[21,1,24,1],[25,1,30,1]]}
["空调末端系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"末端设备","TerminalType",null,"MEnum","S","D2","1. 空调机组 2. 新风机组 3. 风机盘管 4. 辐射末端 5. VAVBOX 6. 远程射流机组 7. 空气幕 8. 地板空调器 9. 多联机 10. 分体空调 99. 其他 （可多选）"]
[null,null,"气流组织","AirDistributionType",null,"MEnum","M","D2","1. 上送上回 2. 上送下回 3. 下送上回 4. 下送下回 99. 其他 （可多选）"]
[null,null,"总额定加湿量","RatedTotD","g/h","Num","R","A2"]
[null,null,"总额定除湿量","RatedTotDeD","g/h","Num","R","A2"]
[null,null,"总额定供冷量","RatedTotCool","kW","Num","M","A2"]
[null,null,"总额定供热量","RatedTotHeat","kW","Num","M","A2"]
[null,null,"总额定空气处理量","RatedTotAirFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"总供冷量","TotCool","kW","Inst","R","M"]
[null,null,"总供热量","TotHeat","kW","Inst","R","M"]
[null,null,"总除湿量","TotDeD","kg/h","Inst","R","M"]
[null,null,"总加湿量","TotD","kg/h","Inst","R","M"]
[null,null,"总耗电功率","TotElecConsumP","kWh","Inst","M","M"]
[null,null,"平均送风温度","AveSupplyAirV","℃","Inst","M","M"]
[null,null,"平均回风温度","AveReturnAirV","℃","Inst","M","M"]
[null,null,"总送风量","TotAirFlow","m3/h","Inst","R","M"]
[null,"瞬时指标","末端开启百分比","TerminalRunPct","%","Inst","M","M"]
[null,null,"末端负载率","TerminalPLR","%","Inst","R","M"]
[null,null,"末端系统COP","SysCOP",null,"Inst","R","M"]
[null,null,"系统输配系数","WTFac",null,"Inst","R","M"]
[null,"累计指标","累计供冷量","AccCool","kWh","Acc","R","M"]
[null,null,"累计供热量","AccHeat ","kWh","Acc","R","M"]
[null,null,"累计除湿量","AccDeD ","kg","Acc","R","M"]
[null,null,"累计加湿量","AccD ","kg","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"IPLV","SysIPLV",null,"Inst","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"VT通风系统","index":3,"n_rows":24,"n_cols":10,"rows_kept":24,"cut":false,"hidden":false,"merged":[[22,0,22,1],[23,0,23,1],[0,0,0,9],[1,0,1,1],[2,0,7,1],[8,0,21,0],[8,1,16,1],[17,1,19,1],[20,1,21,1]]}
["通风系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"洁净等级","CleanLev",null,"Enum","S","D1","1. ISOClass1 2. ISOClass2 3. ISOClass3 4. ISOClass4 5. ISOClass5 6. ISOClass6 7. ISOClass7 8. ISOClass8 9. ISOClass9 99. 其他","ISO14644-1（国际标准）"]
[null,null,"系统过滤效率","SystemFiltEff","%","Num","S","A2"]
[null,null,"送排风类型","SupplyExhaustAirType",null,"Enum","M","D1","1. 只送风 2. 只排风 3. 同时送排风 99. 其他"]
[null,null,"通风方式","VentType",null,"MEnum","R","D2","1. 置换通风 2. 局部通风 3. 混合通风 99. 其他 （可多选）"]
[null,null,"通风动力 ","VentPowerType",null,"Enum","R","D1","1. 自然通风 2. 机械通风 3. 机械+自然通风 99. 其他"]
[null,null,"总额定通风量","TotRatedVent","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"总耗电功率","TotElecConsumP","kW","Inst","M","M"]
[null,null,"总通风量","TotVentFlow","m3/h","Inst","R","M"]
[null,null,"平均送风压力","AveSupplyAirPress","Pa","Inst","R","M"]
[null,null,"平均排风压力","AveExhaustAirPress","Pa","Inst","R","M"]
[null,null,"平均出口风速","AveOutAirV","m/s","Inst","R","M"]
[null,"瞬时指标","风机开启百分比","FanRunPct ","%","Inst","M","M"]
[null,null,"换气次数","AirChangeRate","次/h","Inst","R","M"]
[null,null,"系统输配系数","WTFvt",null,"Inst","R","M"]
[null,"累计指标","累计通风量","AccVent","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"KL厨房排油烟系统","index":4,"n_rows":24,"n_cols":10,"rows_kept":24,"cut":false,"hidden":false,"merged":[[22,0,22,1],[23,0,23,1],[0,0,0,9],[1,0,1,1],[2,0,6,1],[7,0,21,0],[7,1,14,1],[19,1,21,1],[15,1,18,1]]}
["厨房排油烟系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"额定除油烟效率","RatedRemoveLampblackEff","%","Num","S","A2"]
[null,null,"除油烟方式","RemoveLampblackType",null,"MEnum","M","D2","1. 过滤网 2. 活性炭 3. 化学分解 99. 其他 （可多选）"]
[null,null,"抽油烟位置","ExhaustLampblackLocation",null,"Enum","M","D1","1. 顶吸 2. 侧吸 3. 下吸 99. 其他"]
[null,null,"额定排风压力","RatedExhaustLampblackPress","Pa","Num","R","A2"]
[null,null,"额定排油烟风量","RatedExhaustLampblackFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"总耗电功率","TotElecConsumP","kW","Inst","M","M"]
[null,null,"排烟罩平均风压","AveExhaustHoodPress","Pa","Inst","R","M"]
[null,null,"排烟罩平均风速","AveExhaustHoodV","m/s","Inst","R","M"]
[null,null,"总排风量","TotExhaustFlow","m3/h","Inst","R","M"]
[null,"瞬时指标","排烟罩开启百分比","ExhaustHoodRunPct","%","Inst","M","M"]
[null,null,"除油烟效率","RemoveLampblackEff","%","Inst","R","M"]
[null,null,"换气次数","AirChangeRate","次/h","Inst","R","M"]
[null,null,"系统输配系数","SysDisCoeff",null,"Inst","R","M"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计处理风量","AccFlow","m3","Acc","R","M"]
[null,null,"累计除油量","AccRemoveLampblack","kg","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"AD空调人防系统","index":5,"n_rows":25,"n_cols":10,"rows_kept":25,"cut":false,"hidden":false,"merged":[[24,0,24,1],[11,0,22,1],[0,0,0,9],[1,0,1,1],[2,0,10,1],[23,0,23,1]]}
["空调人防系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"战时用途","WartimeFunc",null,"Enum","S","D1","1. 指挥、通信 2. 中心医院及急救医院 3. 人员掩蔽部 4. 专业队装备部 5. 配套工程 99. 其他"]
[null,null,"人员等级","PersonLev",null,"Enum","S","D1","1. 专业队员 2. 一等人员（局级和局级以上） 3. 二等人员 99. 其他"]
[null,null,"抗力等级","ResistanceLev",null,"Enum","S","D1","1. 1级 2. 2级 3. 2b级 4. 3级 5. 4级 6. 4b级 7. 5级 8. 6级 99. 其他"]
[null,null,"防化等级","ChemicalDefenseLev",null,"Enum","S","D1","1. 甲级 2. 乙级 3. 丙级 4. 丁级 99. 其他"]
[null,null,"防护单元面积","DefenseUnitArea","m2","Num","S","A2",null,"上限800m2"]
[null,null,"通风动力方式","VentPowerType",null,"Enum","M","D1","1. 自然通风 2. 机械通风 3. 机械+自然通风 99. 其他"]
[null,null,"通风过滤方式","VentFiltType",null,"Enum","M","D1","1. 隔绝式通风 2. 滤毒式通风 3. 清洁式通风 99. 其他"]
[null,null,"人均新风量标准","RatedFreshAirPerCapita","m3/(h人)","Num","M","A2"]
[null,null,"额定换气次数","RatedAirChangeRate","次/h","Num","M","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"防区人数","DefensePersonNum","人","Inst","R","L"]
[null,null,"总耗电功率","TotElecConsumP","kW","Inst","M","M"]
[null,null,"总通风量","TotVentFlow","m3/h","Inst","R","M"]
[null,null,"送风机开启台数","SupplyFanRunNum","台","Inst","M","M"]
[null,null,"排风机开启台数","ExhaustFanRunNum","台","Inst","M","M"]
[null,null,"换气次数","AirChangeRate","次/h","Inst","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计通风量","AccVentFlow","m3","Acc","R","M"]
["设定参数"]
["报警消息"]