{"text_format":"2","workbook":"xlsx","n_sheets":21,"sheets":["CCCC离心式冷水机组","CCSC螺杆式冷水机组","CCAC吸收式冷水机组","CCAH空调空气源热泵","CCWH空调水源热泵","CCGH空调地源热泵","CCOT冷却塔","CCCP供冷冷冻水泵","CCOP供冷冷却水泵","CCGP供冷乙二醇泵","CCFP供冷补水泵","CCCF供冷定压补水装置","CCHE供冷换热器","CCVD供冷真空脱气机","CCCD供冷水加药装置","CCSD供冷软化水装置","CCTU供冷全程水处理仪","CCST蓄冷热槽","CCDB供冷分水器","CCCL供冷集水器","CCWT供冷水箱"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"CCCC离心式冷水机组","index":0,"n_rows":105,"n_cols":10,"rows_kept":105,"cut":false,"hidden":false,"merged":[[104,0,104,1],[99,0,103,1],[40,1,41,1],[24,1,31,1],[85,1,92,1],[93,1,98,1],[50,1,84,1],[50,0,98,0],[0,0,0,9],[32,1,39,1],[42,1,49,1],[2,0,49,0],[1,0,1,1],[2,1,23,1]]}
["离心式冷水机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定制冷量","RatedCool","kW","Num","S","A2"]
[null,null,"额定COP","RatedCOP",null,"Num","M","A1"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"制冷剂充注量","RefrigerantCharge","kg","Num","R","A2"]
[null,null,"额定制冷剂循环流量","RatedRefrigerantFlow","m3/h","Num","R","A2"]
[null,null,"额定工况制冷循环图","RatedRefrigerateCycle",null,"Attachment","R","F2"]
[null,null,"额定油温","RatedLubeTemp","℃","Num","R","A2"]
[null,null,"额定油量","LubeCap","L","Num","R","A2"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"压缩机","压缩级数","CompressStage","级","Num","R","A2"]
[null,null,"压缩机转子类型","RotorType",null,"Enum","R","D1","1. 角转子 2. 酶标转子 3. 间歇转子 4. 水平转子 5. 连续流转子 99. 其他"]
[null,null,"压缩机最大转速","MaxRPM","rpm","Num","R","A2"]
[null,null,"压缩机最大离心力","MaxCentrifugalF","N","Num","R","A2"]
[null,null,"压缩机额定吸气温度","RatedCompressInTemp","℃","Num","R","A2"]
[null,null,"压缩机额定吸气压力","RatedCompressInPress","MPa","Num","R","A2"]
[null,null,"压缩机额定排气温度","RatedCompressOutTemp","℃","Num","R","A2"]
[null,null,"压缩机额定排气压力","RatedCompressOutPress","MPa","Num","R","A2"]
[null,"蒸发器","设计蒸发器入口水温","DesignEvapWaterInTemp","℃","Num","M","A2"]
[null,null,"设计蒸发器出口水温","DesignEvapWaterOutTemp","℃","Num","M","A2"]
[null,null,"额定蒸发器冷冻水流量","DesignChillWaterFlow","m3/h","Num","M","A2"]
[null,null,"蒸发器水侧换热面积","EvapWaterHeatTransArea","m2","Num","R","A2"]
[null,null,"额定蒸发温度","RatedEvapTemp","℃","Num","R","A2"]
[null,null,"额定蒸发压力","RatedEvapPress","MPa","Num","R","A2"]
[null,null,"蒸发器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"蒸发器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,"节流元件","节流阀种类","ValveType",null,"Enum","R","D1","1. 手动膨胀阀 2. 热力膨胀阀 3. 电子膨胀阀 4. 浮球节流阀 5. 节流孔板 6. 毛细管 99. 其他"]
[null,null,"节流级数","ThrottleStage","级","Num","R","A2"]
[null,"冷凝器","设计冷凝器入口水温","DesignCondWaterInTemp","℃","Num","M","A2"]
[null,null,"设计冷凝器出口水温","DesignCondWaterOutTemp","℃","Num","M","A2"]
[null,null,"额定冷凝器冷却水流量","DesignCoolWaterFlow","m3/h","Num","M","A2"]
[null,null,"冷凝器水侧换热面积","CondWaterHeatTransArea","m2","Num","R","A2"]
[null,null,"额定冷凝温度","RatedCondTemp","℃","Num","R","A2"]
[null,null,"额定冷凝压力","RatedCondPress","MPa","Num","R","A2"]
[null,null,"冷凝器耐压试验压力","CondPressTestPress","MPa","Num","M","A2"]
[null,null,"冷凝器最高允许工作压力","CondMaxAllowPress","MPa","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"瞬时制冷量","CoolP","kW","Inst","M","L"]
[null,null,"工作频率","WorkFreq","Hz","Inst","M","L",null,"有变频功能时"]
[null,null,"蒸发器入口水温","EvapWaterInTemp","℃","Inst","S","L"]
[null,null,"蒸发器出口水温","EvapWaterOutTemp","℃","Inst","S","L"]
[null,null,"蒸发器入口水压","EvapWaterInPress","MPa","Inst","R","L"]
[null,null,"蒸发器出口水压","EvapWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷冻水流量","ChillWaterFlow","m3/h","Inst","M","L"]
[null,null,"蒸发温度","EvapTemp","℃","Inst","M","L"]
[null,null,"蒸发压力","EvapPress","MPa","Inst","M","L"]
[null,null,"压缩机吸气温度","CompressInTemp","℃","Inst","M","L"]
[null,null,"压缩机吸气压力","CompressInPress","MPa","Inst","M","L"]
[null,null,"压缩机排气温度","CompressOutTemp","℃","Inst","M","L"]
[null,null,"压缩机排气压力","CompressOutPress","MPa","Inst","M","L"]
[null,null,"冷凝器入口水温","CondWaterInTemp","℃","Inst","S","L"]
[null,null,"冷凝器出口水温","CondWaterOutTemp","℃","Inst","S","L"]
[null,null,"冷凝器入口水压","CondWaterInPress","MPa","Inst","R","L"]
[null,null,"冷凝器出口水压","CondWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷却水流量","CoolWaterFlow","m3/h","Inst","M","L"]
[null,null,"冷凝温度","CondTemp","℃","Inst","M","L"]
[null,null,"冷凝压力","CondPress","MPa","Inst","M","L"]
[null,null,"油温","LubeTemp","℃","Inst","R","L"]
[null,null,"供油压力","LubePress","MPa","Inst","R","L"]
[null,null,"剩余油量","LubeVolume","L","Inst","R","L"]
[null,"瞬时指标","冷机负载率","PLR","%","Inst","R","M",null,"瞬时制冷量/额定制冷量"]
[null,null,"电流负载率","IPLR","%","Inst","M","M",null,"工作电流/额定电流"]
[null,null,"热不平衡率","HeatUnbalanceRatio","%","Inst","R","M",null,"（冷凝热量-制冷量-功率）/制冷量"]
[null,null,"COP","COP",null,"Inst","M","M",null,"总体效率（DCOP×ICOP）"]
[null,null,"DCOP","DCOP",null,"Inst","R","M",null,"内部效率"]
[null,null,"ICOP","ICOP",null,"Inst","R","M",null,"外部效率"]
[null,null,"蒸发器过热度","EvapSuperheat","℃","Inst","R","M"]
[null,null,"冷凝器过冷度","CondSupercool","℃","Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M",null,"部分负荷性能系数"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"负载率最大值设定","MaxPLRSet","%","Nump","S","L"]
[null,null,"冷冻水出水温度设定值","ChillWaterOutTempSet","℃","Nump","S","L"]
[null,null,"冷冻侧阀门开度设定","ChillValveOpeningSet","%","Nump","S","L"]
[null,null,"冷却侧阀门开度设定","CoolValveOpeningSet","%","Nump","S","L"]
["报警消息"]

{"sheet":"CCSC螺杆式冷水机组","index":1,"n_rows":104,"n_cols":10,"rows_kept":104,"cut":false,"hidden":false,"merged":[[103,0,103,1],[0,0,0,9],[49,0,97,0],[1,0,1,1],[2,0,48,0],[31,1,38,1],[41,1,48,1],[39,1,40,1],[49,1,83,1],[24,1,30,1],[84,1,91,1],[92,1,97,1],[2,1,23,1],[98,0,102,1]]}
["螺杆式冷水机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定制冷量","RatedCool","kW","Num","S","A2"]
[null,null,"额定COP","RatedCOP",null,"Num","M","A1"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"制冷剂充注量","RefrigerantCharge","kg","Num","R","A2"]
[null,null,"额定制冷剂循环流量","RatedRefrigerantFlow","m3/h","Num","R","A2"]
[null,null,"额定工况制冷循环图","RatedRefrigerateCycle",null,"Attachment","R","F2"]
[null,null,"额定油温","RatedLubeTemp","℃","Num","R","A2"]
[null,null,"额定油量","LubeCap","L","Num","R","A2"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"压缩机","压缩级数","CompressStage","级","Num","R","A2"]
[null,null,"压缩机螺杆机头数","ScrewHeadNum","个","Num","M","A2"]
[null,null,"压缩机螺杆齿数","ScrewTeeth","个","Num","R","A2"]
[null,null,"压缩机额定吸气温度","RatedCompressInTemp","℃","Num","R","A2"]
[null,null,"压缩机额定吸气压力","RatedCompressInPress","MPa","Num","R","A2"]
[null,null,"压缩机额定排气温度","RatedCompressOutTemp","℃","Num","R","A2"]
[null,null,"压缩机额定排气压力","RatedCompressOutPress","MPa","Num","R","A2"]
[null,"蒸发器","设计蒸发器入口水温","DesignEvapWaterInTemp","℃","Num","M","A2"]
[null,null,"设计蒸发器出口水温","DesignEvapWaterOutTemp","℃","Num","M","A2"]
[null,null,"额定蒸发器冷冻水流量","DesignChillWaterFlow","m3/h","Num","M","A2"]
[null,null,"蒸发器水侧换热面积","EvapWaterHeatTransArea","m2","Num","R","A2"]
[null,null,"额定蒸发温度","RatedEvapTemp","℃","Num","R","A2"]
[null,null,"额定蒸发压力","RatedEvapPress","MPa","Num","R","A2"]
[null,null,"蒸发器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"蒸发器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,"节流元件","节流阀种类","ValveType",null,"Enum","R","D1","1. 手动膨胀阀 2. 热力膨胀阀 3. 电子膨胀阀 4. 浮球节流阀 5. 节流孔板 6. 毛细管 99. 其他"]
[null,null,"节流级数","ThrottleStage","级","Num","R","A2"]
[null,"冷凝器","设计冷凝器入口水温","DesignCondWaterInTemp","℃","Num","M","A2"]
[null,null,"设计冷凝器出口水温","DesignCondWaterOutTemp","℃","Num","M","A2"]
[null,null,"额定冷凝器冷却水流量","DesignCoolWaterFlow","m3/h","Num","M","A2"]
[null,null,"冷凝器水侧换热面积","CondWaterHeatTransArea","m2","Num","R","A2"]
[null,null,"额定冷凝温度","RatedCondTemp","℃","Num","R","A2"]
[null,null,"额定冷凝压力","RatedCondPress","MPa","Num","R","A2"]
[null,null,"冷凝器耐压试验压力","CondPunctureTestPress","MPa","Num","M","A2"]
[null,null,"冷凝器最高允许工作压力","CondMaxAllowPress","MPa","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"瞬时制冷量","CoolP","kW","Inst","M","L"]
[null,null,"工作频率","WorkFreq","Hz","Inst","M","L",null,"有变频功能时"]
[null,null,"蒸发器入口水温","EvapWaterInTemp","℃","Inst","S","L"]
[null,null,"蒸发器出口水温","EvapWaterOutTemp","℃","Inst","S","L"]
[null,null,"蒸发器入口水压","EvapWaterInPress","MPa","Inst","R","L"]
[null,null,"蒸发器出口水压","EvapWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷冻水流量","ChillWaterFlow","m3/h","Inst","M","L"]
[null,null,"蒸发温度","EvapTemp","℃","Inst","M","L"]
[null,null,"蒸发压力","EvapPress","MPa","Inst","M","L"]
[null,null,"压缩机吸气温度","CompressInTemp","℃","Inst","M","L"]
[null,null,"压缩机吸气压力","CompressInPress","MPa","Inst","M","L"]
[null,null,"压缩机排气温度","CompressOutTemp","℃","Inst","M","L"]
[null,null,"压缩机排气压力","CompressOutPress","MPa","Inst","M","L"]
[null,null,"冷凝器入口水温","CondWaterInTemp","℃","Inst","S","L"]
[null,null,"冷凝器出口水温","CondWaterOutTemp","℃","Inst","S","L"]
[null,null,"冷凝器入口水压","CondWaterInPress","MPa","Inst","R","L"]
[null,null,"冷凝器出口水压","CondWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷却水流量","CoolWaterFlow","m3/h","Inst","M","L"]
[null,null,"冷凝温度","CondTemp","℃","Inst","M","L"]
[null,null,"冷凝压力","CondPress","MPa","Inst","M","L"]
[null,null,"油温","LubeTemp","℃","Inst","R","L"]
[null,null,"供油压力","LubePress","MPa","Inst","R","L"]
[null,null,"剩余油量","LubeVolume","L","Inst","R","L"]
[null,"瞬时指标","冷机负载率","PLR","%","Inst","R","M",null,"瞬时制冷量/额定制冷量"]
[null,null,"电流负载率","IPLR","%","Inst","M","M",null,"工作电流/额定电流"]
[null,null,"热不平衡率","HeatUnbalanceRatio","%","Inst","R","M",null,"（冷凝热量-制冷量-功率）/制冷量"]
[null,null,"COP","COP",null,"Inst","M","M",null,"总体效率（DCOP×ICOP）"]
[null,null,"DCOP","DCOP",null,"Inst","R","M",null,"内部效率"]
[null,null,"ICOP","ICOP",null,"Inst","R","M",null,"外部效率"]
[null,null,"蒸发器过热度","EvapSuperheat","℃","Inst","R","M"]
[null,null,"冷凝器过冷度","CondSupercool","℃","Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M",null,"部分负荷性能系数"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"负载率最大值设定","MaxPLRSet","%","Nump","S","L"]
[null,null,"冷冻水出水温度设定值","ChillWaterOutTempSet","℃","Nump","S","L"]
[null,null,"冷冻侧阀门开度设定","ChillValveOpeningSet","%","Nump","S","L"]
[null,null,"冷却侧阀门开度设定","CoolValveOpeningSet","%","Nump","S","L"]
["报警消息"]

{"sheet":"CCAC吸收式冷水机组","index":2,"n_rows":88,"n_cols":10,"rows_kept":88,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[2,0,40,0],[18,1,20,1],[21,1,22,1],[2,1,17,1],[87,0,87,1],[41,0,81,0],[23,1,30,1],[31,1,32,1],[33,1,40,1],[41,1,67,1],[68,1,75,1],[76,1,81,1],[82,0,86,1]]}
["吸收式冷水机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","热源类型","HeatSourceType",null,"Enum","S","D1","1. 直燃式 2. 热水 3. 蒸汽 99. 其他"]
[null,null,"热源温度","HeatSourceTemp","℃","Num","M","A2"]
[null,null,"额定耗热量","RatedHeatConsum","kW","Num","M","A2"]
[null,null,"额定制冷量","RatedCool","kW","Num","M","A2"]
[null,null,"额定制热量","RatedHeat","kW","Num","M","A2"]
[null,null,"额定制冷COP","RatedCoolCOP",null,"Num","M","A1"]
[null,null,"额定制热COP","RatedHeatCOP",null,"Num","M","A1"]
[null,null,"制冷剂-吸收剂工质对类型","RefrigerantAbsorbentType",null,"Enum","S","D1","1. 氨-水 2. 水-溴化锂 99. 其他"]
[null,null,"制冷剂充注量","RefrigerantCharge","kg","Num","R","A2"]
[null,null,"吸收剂充注量","AbsorbentCharge","kg","Num","R","A2"]
[null,null,"额定制冷剂循环流量","RatedRefrigerantFlow","m3/h","Num","R","A2"]
[null,null,"额定吸收剂再生流量","RatedAbsorbentFlow","m3/h","Num","R","A2"]
[null,null,"吸收剂流动方式","AbsorbentFlowType",null,"Enum","R","E1","1. 并流式 2. 湍流式 99. 其他"]
[null,null,"额定工况制冷循环图","RatedRefrigerateCycle",null,"Attachment","R","F2"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"发生器","发生器级数","GeneratorStage","级","Num","R","A2"]
[null,null,"发生器额定溶液浓度","RatedGeneratorSolutionConcentrate","mol/L","Num","R","A2"]
[null,null,"发生器额定发生压力","RatedGeneratePress","MPa","Num","R","A2"]
[null,"吸收器","吸收器额定溶液浓度","RatedAbsorberSolutionConcentrate","mol/L","Num","R","A2"]
[null,null,"吸收器额定吸收压力","RatedAbsorbPress","MPa","Num","R","A2"]
[null,"蒸发器","设计蒸发器入口冷冻水温","DesignEvapWaterInTemp","℃","Num","M","A2"]
[null,null,"设计蒸发器出口冷冻水温","DesignEvapWaterOutTemp","℃","Num","M","A2"]
[null,null,"额定蒸发器冷冻水流量","DesignChillWaterFlow","m3/h","Num","M","A2"]
[null,null,"蒸发器水侧换热面积","EvapWaterHeatTransArea","m2","Num","R","A2"]
[null,null,"额定蒸发温度","RatedEvapTemp","℃","Num","R","A2"]
[null,null,"额定蒸发压力","RatedEvapPress","MPa","Num","R","A2"]
[null,null,"蒸发器耐压试验压力","EvapPressTestPress","MPa","Num","M","A2"]
[null,null,"蒸发器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,"节流元件","节流阀种类","ValveType",null,"Enum","R","D1","1. 手动膨胀阀 2. 热力膨胀阀 3. 电子膨胀阀 4. 浮球节流阀 5. 节流孔板 6. 毛细管 99. 其他"]
[null,null,"节流级数","ThrottleStage","级","Num","R","A2"]
[null,"冷凝器","设计冷凝器入口冷却水温","DesignCondWaterInTemp","℃","Num","M","A2"]
[null,null,"设计冷凝器出口冷却水温","DesignCondWaterOutTemp","℃","Num","M","A2"]
[null,null,"额定冷凝器冷却水流量","DesignCoolWaterFlow","m3/h","Num","M","A2"]
[null,null,"冷凝器水侧换热面积","CondWaterHeatTransArea","m2","Num","R","A2"]
[null,null,"额定冷凝温度","RatedCondTemp","℃","Num","R","A2"]
[null,null,"额定冷凝压力","RatedCondPress","MPa","Num","R","A2"]
[null,null,"冷凝器耐压试验压力","CondPressTestPress","MPa","Num","M","A2"]
[null,null,"冷凝器最高允许工作压力","CondMaxAllowPress","MPa","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","RunMode",null,"Enumv","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"瞬时耗热量","HeatConsumP","kW","Inst","M","L"]
[null,null,"瞬时制冷量","CoolP","kW","Inst","M","L"]
[null,null,"瞬时制热量","HeatP","kW","Inst","M","L"]
[null,null,"发生器溶液浓度","GeneratorSolutionConcentrate","ppm","Inst","R","L"]
[null,null,"发生压力","GeneratePress","MPa","Inst","R","L"]
[null,null,"吸收器溶液浓度","AbsorberSolution Concentrate","ppm","Inst","R","L"]
[null,null,"吸收压力","AbsorbPress","MPa","Inst","R","L"]
[null,null,"蒸发器入口冷冻水温","EvapWaterInTemp","℃","Inst","S","L"]
[null,null,"蒸发器出口冷冻水温","EvapWaterOutTemp","℃","Inst","S","L"]
[null,null,"蒸发器入口冷冻水压","EvapWaterInPress","MPa","Inst","R","L"]
[null,null,"蒸发器出口冷冻水压","EvapWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷冻水流量","ChillWaterFlow","m3/h","Inst","M","L"]
[null,null,"蒸发温度","EvapTemp","℃","Inst","M","L"]
[null,null,"蒸发压力","EvapPress","MPa","Inst","M","L"]
[null,null,"冷凝器入口冷却水温","CondWaterInTemp","℃","Inst","S","L"]
[null,null,"冷凝器出口冷却水温","CondWaterOutTemp","℃","Inst","S","L"]
[null,null,"冷凝器入口冷却水压","CondWaterInPress","MPa","Inst","R","L"]
[null,null,"冷凝器出口冷却水压","CondWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷却水流量","CoolWaterFlow","m3/h","Inst","M","L"]
[null,null,"冷凝温度","CondTemp","℃","Inst","M","L"]
[null,null,"冷凝压力","CondPress","MPa","Inst","M","L"]
[null,"瞬时指标","冷机负载率","PLR","%","Inst","R","M",null,"瞬时制冷量/额定制冷量"]
[null,null,"耗热负载率","HeatPLR","%","Inst","M","M",null,"瞬时耗热量/额定耗热量"]
[null,null,"热不平衡率","HeatUnbalanceRatio","%","Inst","R","M",null,"（冷凝热量-制冷量-功率）/制冷量"]
[null,null,"COP","COP",null,"Inst","M","M",null,"总体效率（DCOP×ICOP）"]
[null,null,"DCOP","DCOP",null,"Inst","R","M",null,"内部效率"]
[null,null,"ICOP","ICOP",null,"Inst","R","M",null,"外部效率"]
[null,null,"蒸发器过热度","EvapSuperheat","℃","Inst","R","M"]
[null,null,"冷凝器过冷度","CondSupercool","℃","Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M",null,"部分负荷性能系数"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"负载率最大值设定","MaxPLRSet","%","Nump","S","L"]
[null,null,"冷冻水出水温度设定值","ChillWaterOutTempSet","℃","Nump","S","L"]
[null,null,"冷冻侧阀门开度设定","ChillValveOpeningSet","%","Nump","S","L"]
[null,null,"冷却侧阀门开度设定","CoolValveOpeningSet","%","Nump","S","L"]
["报警消息"]

{"sheet":"CCAH空调空气源热泵","index":3,"n_rows":119,"n_cols":10,"rows_kept":119,"cut":false,"hidden":false,"merged":[[113,0,116,1],[117,0,118,1],[0,0,0,9],[44,1,53,1],[54,1,63,1],[64,0,112,0],[2,0,63,0],[1,0,1,1],[64,1,97,1],[98,1,105,1],[106,1,112,1],[2,1,43,1]]}
["空气源热泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"制冷剂充注量","RefrigerantCharge","kg","Num","R","A2"]
[null,null,"额定制冷剂循环流量","RatedRefrigerantFlow","m3/h","Num","R","A2"]
[null,null,"额定工况制冷循环图","RatedRefrigerateCycle",null,"Attachment","R","F2"]
[null,null,"是否有四通阀功能","isFourWayValve",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压缩机类型","CompressorType",null,"Enum","M","D1","1. 活塞式 2. 离心式 3. 螺杆式 99. 其他"]
[null,null,"压缩级数","CompressStage","级","Num","R","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1"]
[null,null,"压缩机额定吸气温度","RatedCompressInTemp","℃","Num","R","A2"]
[null,null,"压缩机额定吸气压力","RatedCompressInPress","MPa","Num","R","A2"]
[null,null,"压缩机额定排气温度","RatedCompressOutTemp","℃","Num","R","A2"]
[null,null,"压缩机额定排气压力","RatedCompressOutPress","MPa","Num","R","A2"]
[null,null,"室内侧载冷剂类型","IndoorMeduimType",null,"Enum","S","D1","1. 空气 2. 水 3. 盐水 99. 其他"]
[null,null,"室内侧载冷剂额定流量","RatedIndoorMeduimFlow","m3/h","Num","M","A2"]
[null,null,"室内侧机组换热面积","IndoorHeatTransArea","m2","Num","R","A2"]
[null,null,"室外侧额定风速","RatedOutdoorWindV","m/s","Num","R","A2"]
[null,null,"室外侧机组换热面积","OutdoorHeatTransArea","m2","Num","R","A2"]
[null,null,"室外侧翅片型式","OutdoorFinType",null,"Enum","R","D1","1. 开窗片 2. 波纹片 99. 其他"]
[null,null,"室外侧翅片间距","OutdoorFinGap ","mm","Num","R","A2"]
[null,null,"室外侧布置形式","OutdoorLayoutType",null,"Enum","R","D1","1. 直型 2. V型 3. W型 99. 其他"]
[null,null,"节流阀种类","ValveType",null,"Enum","R","D1","1. 手动膨胀阀 2. 热力膨胀阀 3. 电子膨胀阀 4. 浮球节流阀 5. 节流孔板 6. 毛细管 99. 其他"]
[null,null,"节流级数","ThrottleStage","级","Num","R","A2"]
[null,null,"融霜方式","DefrostType",null,"Enum","R","D1","1. 压差控制法 2. 温差控制法 3. 温度时间控制法 99. 其他","空气侧换热器容易聚霜，一般采用热气除霜，除霜控制技术有所不同"]
[null,null,"安全保护策略","ProtectMode",null,"Str","R","B1"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"蒸发器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"蒸发器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"冷凝器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"冷凝器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"制冷工况","额定制冷量","RatedCool","kW","Num","S","A2"]
[null,null,"额定制冷COP","RatedCoolCOP",null,"Num","M","A1"]
[null,null,"制冷工况室内侧设计机组入口载冷剂温度","DesignCoolIndoorMediumInTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况室内侧设计机组出口载冷剂温度","DesignCoolIndoorMediumOutTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况额定蒸发温度","RatedCoolEvapTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定蒸发压力","RatedCoolEvapPress","MPa","Num","R","A2"]
[null,null,"制冷工况室外侧设计机组入口空气温度","DesignCoolOutdoorAirInTemp","℃","Num","R","A2",null,"冷凝器"]
[null,null,"制冷工况室外侧设计机组出口空气温度","DesignCoolOutdoorAirOutTemp","℃","Num","R","A2",null,"冷凝器"]
[null,null,"制冷工况额定冷凝温度","RatedCoolCondTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定冷凝压力","RatedCoolCondPress","MPa","Num","R","A2"]
[null,"制热工况","额定制热量","RatedHeat","kW","Num","S","A2"]
[null,null,"额定制热COP","RatedHeatCOP",null,"Num","M","A1"]
[null,null,"制热工况室内侧设计机组入口载冷剂温度","DesignHeatIndoorMediumInTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况室内侧设计机组出口载冷剂温度","DesignHeatIndoorMediumOutTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况额定冷凝温度","RatedHeatCondTemp","℃","Num","R","A2"]
[null,null,"制热工况额定冷凝压力","RatedHeatCondPress","MPa","Num","R","A2"]
[null,null,"制热工况室外侧设计机组入口空气温度","DesignHeatOutdoorAirInTemp","℃","Num","R","A2",null,"蒸发器"]
[null,null,"制热工况室外侧设计机组出口空气温度","DesignHeatOutdoorAirOutTemp","℃","Num","R","A2",null,"蒸发器"]
[null,null,"制热工况额定蒸发温度","RatedHeatEvapTemp","℃","Num","R","A2"]
[null,null,"制热工况额定蒸发压力","RatedHeatEvapPress","MPa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","RunMode",null,"Enumv","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","S","L",null,"三相有功功率"]
[null,null,"瞬时制冷量","CoolP","kW","Inst","S","L"]
[null,null,"瞬时制热量","HeatP","kW","Inst","S","L"]
[null,null,"工作频率","WorkFreq","Hz","Inst","R","L",null,"有变频功能时"]
[null,null,"室内侧机组入口载冷剂温度","IndoorMediumInTemp","℃","Inst","S","L"]
[null,null,"室内侧机组出口载冷剂温度","IndoorMediumOutTemp","℃","Inst","S","L"]
[null,null,"室内侧机组入口载冷剂压力","IndoorMediumInPress","MPa","Inst","R","L"]
[null,null,"室内侧机组出口载冷剂压力","IndoorMediumOutPress","MPa","Inst","R","L"]
[null,null,"室内侧载冷剂流量","IndoorMediumFlow","m3/h","Inst","M","L"]
[null,null,"压缩机吸气温度","CompressInTemp","℃",null,null,"L"]
[null,null,"压缩机吸气压力","CompressInPress","MPa",null,null,"L"]
[null,null,"压缩机排气温度","CompressOutTemp","℃",null,null,"L"]
[null,null,"压缩机排气压力","CompressOutPress","MPa",null,null,"L"]
[null,null,"室外侧机组入口空气温度","OutdoorAirInTemp","℃","Inst","M","L"]
[null,null,"室外侧机组出口空气温度","OutdoorAirOutTemp","℃","Inst","M","L"]
[null,null,"室外侧机组入口空气压力","OutdoorAirInPress","Pa","Inst","R","L"]
[null,null,"室外侧机组出口空气压力","OutdoorAirOutPress","Pa","Inst","R","L"]
[null,null,"室外侧风速","OutdoorWindV","m/s","Inst","R","L"]
[null,null,"蒸发温度","EvapTemp","℃","Inst","M","L"]
[null,null,"蒸发压力","EvapPress","MPa","Inst","M","L"]
[null,null,"冷凝温度","CondTemp","℃","Inst","M","L"]
[null,null,"冷凝压力","CondPress","MPa","Inst","M","L"]
[null,"瞬时指标","热泵负载率","PLR","%","Inst","R","M",null,"实际供冷（热）量/额定供冷（热）量"]
[null,null,"电流负载率","IPLR","%","Inst","M","M",null,"实际电流/额定电流"]
[null,null,"热不平衡率","HeatUnbalanceRate","%","Inst","R","M",null,"（冷凝热量-制冷量-功率）/制冷量"]
[null,null,"COP","COP",null,"Inst","M","M",null,"总体效率（DCOP×ICOP）"]
[null,null,"DCOP","DCOP",null,"Inst","R","M",null,"内部效率"]
[null,null,"ICOP","ICOP",null,"Inst","R","M",null,"外部效率"]
[null,null,"蒸发器过热度","EvapSuperheat","℃","Inst","R","M"]
[null,null,"冷凝器过冷度","CondSupercool","℃","Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M",null,"部分负荷性能系数"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"运行模式设定","RunModeSet",null,"Enump","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"室内侧机组载冷剂出口温度设定","IndoorMediumOutTempSet","℃","Nump","S","L"]
["报警消息",null,"制冷故障","CoolingFaultAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"制热故障","HeatingFaultAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CCWH空调水源热泵","index":4,"n_rows":115,"n_cols":10,"rows_kept":115,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[2,0,59,0],[40,1,49,1],[50,1,59,1],[2,1,39,1],[113,0,114,1],[102,1,108,1],[60,0,108,0],[60,1,93,1],[94,1,101,1],[109,0,112,1]]}
["水源热泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"制冷剂充注量","RefrigerantCharge","kg","Num","R","A2"]
[null,null,"额定制冷剂循环流量","RatedRefrigerantFlow","m3/h","Num","R","A2"]
[null,null,"额定工况制冷循环图","RatedRefrigerateCycle",null,"Attachment","R","F2"]
[null,null,"是否有四通阀功能","isFourWayValve",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压缩机类型","CompressorType",null,"Enum","M","D1","1. 活塞式 2. 离心式 3. 螺杆式 99. 其他"]
[null,null,"压缩级数","CompressStage","级","Num","R","A2"]
[null,null,"压缩机额定吸气温度","RatedCompressInTemp","℃","Num","R","A2"]
[null,null,"压缩机额定吸气压力","RatedCompressInPress","MPa","Num","R","A2"]
[null,null,"压缩机额定排气温度","RatedCompressOutTemp","℃","Num","R","A2"]
[null,null,"压缩机额定排气压力","RatedCompressOutPress","MPa","Num","R","A2"]
[null,null,"室内侧载冷剂类型","IndoorMeduimType",null,"Enum","S","D1","1. 空气 2. 水 3. 盐水 99. 其他"]
[null,null,"室内侧载冷剂额定流量","RatedIndoorMeduimFlow","m3/h","Num","M","A2"]
[null,null,"室内侧机组换热面积","IndoorHeatTransArea","m2","Num","R","A2"]
[null,null,"水源侧额定冷却水流量","RatedOutdoorWaterFlow","m3/h","Num","R","A2"]
[null,null,"水源侧机组换热面积","OutdoorHeatTransArea","m2","Num","R","A2"]
[null,null,"水源类型","WaterSourceType",null,"Enum","S","D1","1. 地表水 2. 地下水 99. 其他"]
[null,null,"节流阀种类","ValveType",null,"Enum","R","D1","1. 手动膨胀阀 2. 热力膨胀阀 3. 电子膨胀阀 4. 浮球节流阀 5. 节流孔板 6. 毛细管 99. 其他"]
[null,null,"节流级数","ThrottleStage","级","Num","R","A2"]
[null,null,"安全保护策略","ProtectMode",null,"Str","R","B1"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"蒸发器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"蒸发器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"冷凝器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"冷凝器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"制冷工况","额定制冷量","RatedCool","kW","Num","S","A2"]
[null,null,"额定制冷COP","RatedCoolCOP",null,"Num","M","A1"]
[null,null,"制冷工况额定室内侧机组入口载冷剂温度","DesignCoolIndoorMediumInTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况额定室内侧机组出口载冷剂温度","DesignCoolIndoorMediumOutTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况额定蒸发温度","RatedCoolEvapTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定蒸发压力","RatedCoolEvapPress","MPa","Num","R","A2"]
[null,null,"制冷工况额定水源侧机组入口冷却水温度","DesignCoolOutdoorWaterInTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制冷工况额定水源侧机组出口冷却水温度","DesignCoolOutdoorWaterOutTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制冷工况额定冷凝温度","RatedCoolCondTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定冷凝压力","RatedCoolCondPress","MPa","Num","R","A2"]
[null,"制热工况","额定制热量","RatedHeat","kW","Num","S","A2"]
[null,null,"额定制热COP","RatedHeatCOP",null,"Num","M","A1"]
[null,null,"制热工况额定室内侧机组入口载冷剂温度","DesignHeatIndoorMediumInTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况额定室内侧机组出口载冷剂温度","DesignHeatIndoorMediumOutTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况额定冷凝温度","RatedHeatCondTemp","℃","Num","R","A2"]
[null,null,"制热工况额定冷凝压力","RatedHeatCondPress","MPa","Num","R","A2"]
[null,null,"制热工况额定水源侧机组入口冷却水温度","DesignHeatOutdoorWaterInTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制热工况额定水源侧机组出口冷却水温度","DesignHeatOutdoorWaterOutTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制热工况额定蒸发温度","RatedHeatEvapTemp","℃","Num","R","A2"]
[null,null,"制热工况额定蒸发压力","RatedHeatEvapPress","MPa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","RunMode",null,"Enumv","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"瞬时制冷量","CoolP","kW","Inst","M","L"]
[null,null,"瞬时制热量","HeatP","kW","Inst","M","L"]
[null,null,"工作频率","WorkFreq","Hz","Inst","R","L",null,"有变频功能时"]
[null,null,"室内侧机组入口载冷剂温度","IndoorMediumInTemp","℃","Inst","S","L"]
[null,null,"室内侧机组出口载冷剂温度","IndoorMediumOutTemp","℃","Inst","S","L"]
[null,null,"室内侧机组入口载冷剂压力","IndoorMediumInPress","MPa","Inst","R","L"]
[null,null,"室内侧机组出口载冷剂压力","IndoorMediumOutPress","MPa","Inst","R","L"]
[null,null,"室内侧载冷剂流量","IndoorMediumFlow","m3/h","Inst","M","L"]
[null,null,"压缩机吸气温度","CompressInTemp","℃","Inst","M","L"]
[null,null,"压缩机吸气压力","CompressInPress","MPa","Inst","M","L"]
[null,null,"压缩机排气温度","CompressOutTemp","℃","Inst","M","L"]
[null,null,"压缩机排气压力","CompressOutPress","MPa","Inst","M","L"]
[null,null,"水源侧机组入口冷却水温度","OutdoorWaterInTemp","℃","Inst","S","L"]
[null,null,"水源侧机组出口冷却水温度","OutdoorWaterOutTemp","℃","Inst","S","L"]
[null,null,"水源侧机组入口冷却水压力","OutdoorWaterInPress","MPa","Inst","R","L"]
[null,null,"水源侧机组出口冷却水压力","OutdoorWaterOutPress","MPa","Inst","R","L"]
[null,null,"水源侧冷却水流量","OutdoorWaterFlow","m3/h","Inst","M","L"]
[null,null,"蒸发温度","EvapTemp","℃","Inst","M","L"]
[null,null,"蒸发压力","EvapPress","MPa","Inst","M","L"]
[null,null,"冷凝温度","CondTemp","℃","Inst","M","L"]
[null,null,"冷凝压力","CondPress","MPa","Inst","M","L"]
[null,"瞬时指标","热泵负载率","PLR","%","Inst","R","M",null,"实际供冷（热）量/额定供冷（热）量"]
[null,null,"电流负载率","IPLR","%","Inst","M","M",null,"实际电流/额定电流"]
[null,null,"热不平衡率","HeatUnbalanceRate","%","Inst","R","M",null,"（冷凝热量-制冷量-功率）/制冷量"]
[null,null,"COP","COP",null,"Inst","M","M",null,"总体效率（DCOP×ICOP）"]
[null,null,"DCOP","DCOP",null,"Inst","R","M",null,"内部效率"]
[null,null,"ICOP","ICOP",null,"Inst","R","M",null,"外部效率"]
[null,null,"蒸发器过热度","EvapSuperheat","℃","Inst","R","M"]
[null,null,"冷凝器过冷度","CondSupercool","℃","Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M",null,"部分负荷性能系数"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"运行模式设定","RunModeSet",null,"Enump","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"室内侧机组载冷剂出口温度设定","IndoorMediumOutTempSet","℃","Nump","S","L"]
["报警消息",null,"制冷故障","CoolingFaultAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"制热故障","HeatingFaultAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CCGH空调地源热泵","index":5,"n_rows":123,"n_cols":10,"rows_kept":123,"cut":false,"hidden":false,"merged":[[117,0,120,1],[121,0,122,1],[1,0,1,1],[67,1,100,1],[0,0,0,9],[101,1,108,1],[2,0,66,0],[47,1,56,1],[57,1,66,1],[67,0,116,0],[109,1,116,1],[2,1,46,1]]}
["地源热泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"制冷剂充注量","RefrigerantCharge","kg","Num","R","A2"]
[null,null,"额定制冷剂循环流量","RatedRefrigerantFlow","m3/h","Num","R","A2"]
[null,null,"额定工况制冷循环图","RatedRefrigerateCycle",null,"Attachment","R","F2"]
[null,null,"是否有四通阀功能","isFourWayValve",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压缩机类型","CompressorType",null,"Enum","M","D1","1. 活塞式 2. 离心式 3. 螺杆式 99. 其他"]
[null,null,"压缩级数","CompressStage","级","Num","R","A2"]
[null,null,"压缩机额定吸气温度","RatedCompressInTemp","℃","Num","R","A2"]
[null,null,"压缩机额定吸气压力","RatedCompressInPress","MPa","Num","R","A2"]
[null,null,"压缩机额定排气温度","RatedCompressOutTemp","℃","Num","R","A2"]
[null,null,"压缩机额定排气压力","RatedCompressOutPress","MPa","Num","R","A2"]
[null,null,"室内侧载冷剂类型","IndoorMeduimType",null,"Enum","S","D1","1. 空气 2. 水 3. 盐水 99. 其他"]
[null,null,"室内侧载冷剂额定流量","RatedIndoorMeduimFlow","m3/h","Num","M","A2"]
[null,null,"室内侧机组换热面积","IndoorHeatTransArea","m2","Num","R","A2"]
[null,null,"地源侧循环液类型","OutdoorMeduimType",null,"Enum","S","D1","1. 水 2. 防冻液 99. 其他"]
[null,null,"地源侧循环液额定流量","RatedOutdoorMeduimFlow","m3/h","Num","M","A2"]
[null,null,"地源侧机组换热面积","OutdoorHeatTransArea","m3","Num","R","A2",null,"制冷剂-地埋管循环液"]
[null,null,"地埋管设置形式","BuriedPipeType",null,"Enum","M","D1","1. 水平埋管 2. 垂直埋管 99. 其他"]
[null,null,"地埋管距地深度","BuriedPipeDepth","m","Num","M","A2"]
[null,null,"地埋管材质","BuriedPipeMaterial",null,"Enum","R","D1","1. 聚乙烯 2. 聚丁烯 99. 其他"]
[null,null,"地埋管外径","BuriedPipeOutDiameter","mm","Num","R","A2"]
[null,null,"地埋管壁厚","BuriedPipeThick","mm","Num","R","A2"]
[null,null,"地埋管长度","BuriedPipeLength","m","Num","R","A2"]
[null,null,"地埋管间距","BuriedPipeGap","m","Num","R","A2"]
[null,null,"节流阀种类","ValveType",null,"Enum","R","D1","1. 手动膨胀阀 2. 热力膨胀阀 3. 电子膨胀阀 4. 浮球节流阀 5. 节流孔板 6. 毛细管 99. 其他"]
[null,null,"节流级数","ThrottleStage","级","Num","R","A2"]
[null,null,"安全保护策略","ProtectMode",null,"Str","R","B1"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"蒸发器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"蒸发器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"冷凝器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"冷凝器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"制冷工况","额定制冷量","RatedCool","kW","Num","S","A2"]
[null,null,"额定制冷COP","RatedCoolCOP",null,"Num","M","A1"]
[null,null,"制冷工况额定室内侧机组入口载冷剂温度","DesignCoolIndoorMediumInTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况额定室内侧机组出口载冷剂温度","DesignCoolIndoorMediumOutTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况额定蒸发温度","RatedCoolEvapTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定蒸发压力","RatedCoolEvapPress","MPa","Num","R","A2"]
[null,null,"制冷工况额定地源侧机组入口循环液温度","DesignCoolOutdoorMediumInTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制冷工况额定地源侧机组出口循环液温度","DesignCoolOutdoorMediumOutTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制冷工况额定冷凝温度","RatedCoolCondTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定冷凝压力","RatedCoolCondPress","MPa","Num","R","A2"]
[null,"制热工况","额定制热量","RatedHeat","kW","Num","S","A2"]
[null,null,"额定制热COP","RatedHeatCOP",null,"Num","M","A1"]
[null,null,"制热工况额定室内侧机组入口载冷剂温度","DesignHeatIndoorMediumInTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况额定室内侧机组出口载冷剂温度","DesignHeatIndoorMediumOutTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况额定冷凝温度","RatedHeatCondTemp","℃","Num","R","A2"]
[null,null,"制热工况额定冷凝压力","RatedHeatCondPress","MPa","Num","R","A2"]
[null,null,"制热工况额定地源侧机组入口循环液温度","DesignHeatOutdoorMediumInTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制热工况额定地源侧机组出口循环液温度","DesignHeatOutdoorMediumOutTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制热工况额定蒸发温度","RatedHeatEvapTemp","℃","Num","R","A2"]
[null,null,"制热工况额定蒸发压力","RatedHeatEvapPress","MPa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","RunMode",null,"Enumv","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"瞬时制冷量","CoolP","kW","Inst","M","L"]
[null,null,"瞬时制热量","HeatP","kW","Inst","M","L"]
[null,null,"工作频率","WorkFreq","Hz","Inst","R","L",null,"有变频功能时"]
[null,null,"室内侧机组入口载冷剂温度","IndoorMediumInTemp","℃","Inst","S","L"]
[null,null,"室内侧机组出口载冷剂温度","IndoorMediumOutTemp","℃","Inst","S","L"]
[null,null,"室内侧机组入口载冷剂压力","IndoorMediumInPress","MPa","Inst","R","L"]
[null,null,"室内侧机组出口载冷剂压力","IndoorMediumOutPress","MPa","Inst","R","L"]
[null,null,"室内侧载冷剂流量","IndoorMediumFlow","m3/h","Inst","M","L"]
[null,null,"压缩机吸气温度","CompressInTemp","℃","Inst","M","L"]
[null,null,"压缩机吸气压力","CompressInPress","MPa","Inst","M","L"]
[null,null,"压缩机排气温度","CompressOutTemp","℃","Inst","M","L"]
[null,null,"压缩机排气压力","CompressOutPress","MPa","Inst","M","L"]
[null,null,"地源侧机组入口循环液温度","OutdoorMediumInTemp","℃","Inst","M","L"]
[null,null,"地源侧机组出口循环液温度","OutdoorMediumOutTemp","℃","Inst","M","L"]
[null,null,"地源侧机组入口载冷剂压力","OutdoorMediumInPress","MPa","Inst","R","L"]
[null,null,"地源侧机组出口载冷剂压力","OutdoorMediumOutPress","MPa","Inst","R","L"]
[null,null,"地源侧循环液流量","OutdoorMediumFlow","m3/h","Inst","M","L"]
[null,null,"蒸发温度","EvapTemp","℃","Inst","M","L"]
[null,null,"蒸发压力","EvapPress","MPa","Inst","M","L"]
[null,null,"冷凝温度","CondTemp","℃","Inst","M","L"]
[null,null,"冷凝压力","CondPress","MPa","Inst","M","L"]
[null,"瞬时指标","热泵负载率","PLR","%","Inst","R","M",null,"实际供冷（热）量/额定供冷（热）量"]
[null,null,"电流负载率","IPLR","%","Inst","M","M",null,"实际电流/额定电流"]
[null,null,"热不平衡率","HeatUnbalanceRate","%","Inst","R","M",null,"（冷凝热量-制冷量-功率）/制冷量"]
[null,null,"COP","COP",null,"Inst","M","M",null,"总体效率（DCOP×ICOP）"]
[null,null,"DCOP","DCOP",null,"Inst","R","M",null,"内部效率"]
[null,null,"ICOP","ICOP",null,"Inst","R","M",null,"外部效率"]
[null,null,"蒸发器过热度","EvapSuperheat","℃","Inst","R","M"]
[null,null,"冷凝器过冷度","CondSupercool","℃","Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M",null,"部分负荷性能系数"]
[null,null,"年累计冷热平衡率","AccHeatBalanceRate",null,"Inst","R","M",null,"年累计地埋管放冷量/年累计地埋管放热量"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"运行模式设定","RunModeSet",null,"Enump","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"室内侧机组载冷剂出口温度设定","IndoorMediumOutTempSet","℃","Nump","S","L"]
["报警消息",null,"制冷故障","CoolingFaultAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"制热故障","HeatingFaultAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CCOT冷却塔","index":6,"n_rows":86,"n_cols":10,"rows_kept":86,"cut":false,"hidden":false,"merged":[[77,0,82,1],[83,0,85,1],[1,0,1,1],[0,0,0,9],[2,0,36,0],[37,0,76,0],[37,1,53,1],[62,1,66,1],[67,1,68,1],[54,1,61,1],[72,1,76,1],[26,1,36,1],[69,1,71,1],[2,1,25,1]]}
["冷却塔"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","原理类型","PrincipleType",null,"Enum","S","D1","1. 湿式（开式） 2. 干式（闭式） 3. 干湿式 99. 其他"]
[null,null,"通风方式","VentType",null,"Enum","M","D1","1. 机械通风 2. 自然通风 3. 混合通风 99. 其他"]
[null,null,"水流动方向","WaterFlowType",null,"Enum","M","D1","1. 横流（直交流） 2. 逆流 3. 混流（叉流） 99. 其他"]
[null,null,"冷却塔形状","ShapeType",null,"Enum","M","D1","1. 圆形 2. 方形 99. 其他"]
[null,null,"噪声级别","NoiseLev",null,"Enum","R","D1","1. 普通型 2. 低噪型 3. 超低噪型 4. 超静音型 99. 其他"]
[null,null,"其他特殊类型","OtherType",null,"Enum","R","D1","1. 无 2. 喷流式 3. 无风机 99. 其他"]
[null,null,"额定循环水量","RatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"额定进塔水温","RatedWaterInTemp","℃","Num","M","A2"]
[null,null,"额定出塔水温","RatedWaterOutTemp","℃","Num","M","A2"]
[null,null,"塔入口阀门类型","InValveType",null,"Enum","R","D1","1. 开关阀 2. 调节阀 99. 其他"]
[null,null,"塔出口阀门类型","OutValveType",null,"Enum","R","D1","1. 开关阀 2. 调节阀 99. 其他"]
[null,null,"塔高","TowerHeight","m","Num","R","A2",null,"上下水盘水面高差"]
[null,null,"额定散热量","RatedHeatRelease","kW","Num","M","A2"]
[null,null,"补水方式","FillingWaterType",null,"Enum","R","D1","1. 浮球阀补水  2. 定时补水  99. 其他"]
[null,null,"电机防护等级","FanIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"冷却水理论压力损失","CoolWaterRatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"风机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"风机个数","FanNum","个","Num","S","A2"]
[null,null,"风机额定电压","RatedFanU","V","Num","S","A2"]
[null,null,"单台风机额定电流","RatedFanI","A","Num","M","A2"]
[null,null,"单台风机额定功率","RatedFanP","kW","Num","S","A2"]
[null,null,"风机类型","FanType",null,"Enum","S","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"风机直径","FanDiameter","mm","Num","R","A2"]
[null,null,"风机额定转速","RatedFanRPM","rpm","Num","M","A2"]
[null,null,"额定风量","RatedFanAirFlow","m3/h","Num","M","A2"]
[null,null,"额定扬程","RatedFanHead","Pa","Num","R","A2"]
[null,null,"控制方式","FanCtrlMode",null,"Enum","R","D1","1. 星三角启动 2. 软启动 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"风机开启台数","FanRunNum","台","Inst","S","L"]
[null,null,"风机运行频率","FanWorkFreq","Hz","Insts","S","L"]
[null,null,"风机档位","FanGear",null,"Enumvs","S","L","1. 高档 2. 中档 3. 低档 99. 其他"]
[null,"水侧","进塔水阀开度","InValveOpening","%","Inst","R","L"]
[null,null,"进塔水温","WaterInTemp","℃","Inst","M","L"]
[null,null,"进塔水压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出塔水阀开度","OutValveOpening","%","Inst","R","L"]
[null,null,"出塔水温","WaterOutTemp","℃","Inst","M","L"]
[null,null,"出塔水压力","WaterOutPress","MPa","Inst","R","L"]
[null,null,"瞬时水流量","WaterFlow","m3/h","Inst","M","L"]
[null,null,"瞬时排热量","HeatRelease","kW","Inst","R","L"]
[null,"空气侧","进塔空气温度","AirInTemp","℃","Inst","R","L"]
[null,null,"进塔空气湿度","AirInRH","%RH","Inst","R","L"]
[null,null,"出塔空气温度","AirOutTemp","℃","Inst","R","L"]
[null,null,"出塔空气湿度","AirOutRH","%RH","Inst","R","L"]
[null,null,"瞬时风量","AirFlow","m3/h","Inst","R","L"]
[null,"塔盘水位","冷却塔上水盘水位","HighTrayWaterLev","m","Inst","R","L"]
[null,null,"冷却塔下水盘水位","LowTrayWaterLev","m","Inst","R","L"]
[null,"瞬时指标","冷却塔散热综合效率","CoolTowerEff","%","Inst","R","M",null,"冷却侧排热量/冷却塔风机的耗电量"]
[null,null,"冷却塔风水比","AirWaterRatio",null,"Inst","R","M"]
[null,null,"冷却塔阻力","Resistance","MPa","Inst","R","M"]
[null,"累计指标","累计散热量","AccHeatRelease","kWh","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计开启时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"风机频率设定","FanFreqSet","Hz","Numps","S","L"]
[null,null,"进塔水阀开度设定","InValveOpeningSet","%","Nump","S","L"]
[null,null,"极限温度设定","LimitTempSet","℃","Nump","S","L"]
[null,null,"出塔水温设定","WaterOutTempSet","℃","Nump","S","L"]
[null,null,"进出塔水温差设定","WaterInOutDetaTempSet","℃","Nump","S","L"]
["报警消息",null,"风机频率低于下限报警","FanFreqUnderLimitAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"出塔水温低于冷机保护温度报警","WaterOutTempUnderChillerProtectAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"出塔水温低于极限温度报警","WaterOutTempUnderLimitTempAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CCCP供冷冷冻水泵","index":7,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[76,0,77,1],[73,0,75,1],[0,0,0,9],[41,0,72,0],[41,1,61,1],[62,1,66,1],[1,0,1,1],[2,0,40,0],[37,1,40,1],[67,1,72,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息",null,"频率超出上限报警","FreqOverUpLimitAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"频率超出下限报警","FreqUnderDownLimitAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CCOP供冷冷却水泵","index":8,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[73,0,75,1],[76,0,77,1],[67,1,72,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息",null,"频率超出上限报警","FreqOverUpLimitAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"频率超出下限报警","FreqUnderDownLimitAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CCGP供冷乙二醇泵","index":9,"n_rows":77,"n_cols":10,"rows_kept":77,"cut":false,"hidden":false,"merged":[[67,1,72,1],[73,0,75,1],[76,0,76,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S",null,"0. 关闭 1. 开启"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S",null,"1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息"]

{"sheet":"CCFP供冷补水泵","index":10,"n_rows":77,"n_cols":10,"rows_kept":77,"cut":false,"hidden":false,"merged":[[67,1,72,1],[73,0,75,1],[76,0,76,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S",null,"0. 关闭 1. 开启"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S",null,"1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息"]

{"sheet":"CCCF供冷定压补水装置","index":11,"n_rows":23,"n_cols":10,"rows_kept":23,"cut":false,"hidden":false,"merged":[[22,0,22,1],[0,0,0,9],[1,0,1,1],[11,0,20,1],[21,0,21,1],[2,0,10,1]]}
["定压补水装置"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"最大工作压力","MaxWorkPress","MPa","Num","M","A2"]
[null,null,"定压精度","ConstantPressAccuracy","MPa","Num","R","A2"]
[null,null,"给水压力","SupplyWaterPress","MPa","Num","M","A2"]
[null,null,"总容积","TotCap","m3","Num","M","A2"]
[null,null,"调节容积","AdjustCap","m3","Num","R","A2"]
[null,null,"供水能力范围","SupplyWaterRange","m3/h","Num","R","A6"]
[null,null,"排气模式","ExhaustType",null,"Enum","R","D1","1. 常压隔膜罐排气 2. 真空排气 99. 其他"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"水箱水量","TankVolume","m3","Inst","M","L"]
[null,null,"水箱压力","TankPress","MPa","Inst","M","L"]
[null,null,"补水状态","FillingStatus",null,"Boolv","M","L","0. 未补水 1. 补水"]
[null,null,"日补水量","DayFilling","m3","Inst","R","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CCHE供冷换热器","index":12,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":false,"merged":[[42,0,42,1],[43,0,43,1],[0,0,0,9],[1,0,1,1],[39,1,41,1],[2,0,16,1],[17,0,41,0],[17,1,38,1]]}
["换热器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"换热介质类型","MediumType",null,"Enum","S","D1","1. 水-水换热 2. 水-汽换热 99. 其他"]
[null,null,"结构类型","StructureType",null,"Enum","M","D1","1. 夹套式换热器 2. 蛇管式换热器 3. 套管式换热器 4. 列管式换热器 5. 板片式换热器 6. 非金属换热器 99. 其他"]
[null,null,"设计换热量","DesignHeatTrans","kW","Num","M","A2"]
[null,null,"换热面积","HeatTransArea","m2","Num","R","A2"]
[null,null,"高温侧设计水流量","DesignHighFlow","m3/h","Num","R","A2"]
[null,null,"高温侧设计进水温度","DesignHighInTemp","℃","Num","R","A2"]
[null,null,"高温侧设计出水温度","DesignHighOutTemp","℃","Num","R","A2"]
[null,null,"高温侧设计供蒸汽压力","DesignHighVaporPress","MPa","Num","R","A2",null,"水-汽换热时"]
[null,null,"高温侧设计供蒸汽流量","DesignHighVaporFlow","t/h","Num","R","A2",null,"水-汽换热时"]
[null,null,"低温侧设计水流量","DesignLowFlow","m3/h","Num","R","A2"]
[null,null,"低温侧设计进水温度","DesignLowInTemp","℃","Num","R","A2"]
[null,null,"低温侧设计出水温度","DesignLowOutTemp","℃","Num","R","A2"]
[null,null,"传热系数","HeatTransCoeff","W/(m2K)","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"换热功率","HeatTransP","kW","Inst","R","L"]
[null,null,"高温侧进水温度","HighInTemp","℃","Inst","S","L"]
[null,null,"高温侧出水温度","HighOutTemp","℃","Inst","S","L"]
[null,null,"高温侧水阀开度","HighValveOpening","%","Inst","R","L"]
[null,null,"高温侧瞬时流量","HighFlow","m3/h","Inst","M","L"]
[null,null,"高温侧进水压力","HighInPress","MPa","Inst","R","L"]
[null,null,"高温侧出水压力","HighOutPress","MPa","Inst","R","L"]
[null,null,"高温侧供蒸汽压力","HighVaporPress","MPa","Inst","S","L",null,"水-汽换热时"]
[null,null,"高温侧凝水温度","HighCondenseWaterTemp","℃","Inst","M","L",null,"水-汽换热时"]
[null,null,"高温侧蒸汽阀开度","HighVaporValveOpening","%","Inst","R","L",null,"水-汽换热时"]
[null,null,"高温侧瞬时蒸汽流量","HighVaporFlow","t/h","Inst","M","L",null,"水-汽换热时"]
[null,null,"低温侧进水温度","LowInTemp","℃","Inst","S","L"]
[null,null,"低温侧出水温度","LowOutTemp","℃","Inst","S","L"]
[null,null,"低温侧水阀状态","LowValveOpening","%","Inst","R","L"]
[null,null,"低温侧瞬时流量","LowFlow","m3/h","Inst","M","L"]
[null,null,"低温侧进水压力","LowInPress","MPa","Inst","R","L"]
[null,null,"低温侧出水压力","LowOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","换热器高温侧阻力","HighResistance","MPa","Inst","R","M"]
[null,null,"换热器低温侧阻力","LowResistance","MPa","Inst","R","M"]
[null,null,"换热效率","HeatTransEff","%","Inst","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CCVD供冷真空脱气机","index":13,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":false,"merged":[[42,0,42,1],[43,0,43,1],[0,0,0,9],[1,0,1,1],[2,0,19,1],[20,0,41,0],[20,1,34,1],[37,1,41,1],[35,1,36,1]]}
["真空脱气机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"处理能力","ProcessCapacity","m3/h","Num","M","A2"]
[null,null,"额定游离气体析除率","RatedFreeGasRemoveRatio","%","Num","M","A2"]
[null,null,"额定溶解气体析除率","RatedDissolvedGasRemoveRatio","%","Num","M","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","MediumFlow","m3/h","Inst","M","L"]
[null,null,"工作水温","MediumTemp","℃","Inst","R","L"]
[null,null,"工作压力","MediumPress","MPa","Inst","R","L"]
[null,null,"进水游离气体含量","InFreeGas","mL/m3","Inst","R","L"]
[null,null,"出水游离气体含量","OutFreeGas","mL/m3","Inst","R","L"]
[null,null,"进水溶解气体含量","InDissolvedGas","mL/m3","Inst","R","L"]
[null,null,"出水溶解气体含量","OutDissolvedGas","mL/m3","Inst","R","L"]
[null,"瞬时指标","游离气体析除率","FreeGasRemoveRatio","h","Inst","R","M"]
[null,null,"溶解气体析除率","DissolvedGasRemoveRatio","h","Inst","R","M"]
[null,"累计指标","累计处理水量","AccMediumVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CCCD供冷水加药装置","index":14,"n_rows":37,"n_cols":10,"rows_kept":37,"cut":false,"hidden":false,"merged":[[36,0,36,1],[2,0,16,1],[0,0,0,9],[1,0,1,1],[17,0,34,1],[35,0,35,1]]}
["水加药装置"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定水流量","RatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"加药方式","ChemicalFeedType",null,"Enum","M","D1","1. 人工投料 2. 自动投料 99. 其他"]
[null,null,"配药用水压力","RatedChemicalWaterPress","MPa","Num","R","A2"]
[null,null,"配药用水温度","RatedChemicalWaterTemp","℃","Num","R","A2"]
[null,null,"稳定剂计量箱容积","StabilizerTankCap","m3","Num","R","A2"]
[null,null,"稳定剂计量泵流量","StabilizerPumpFlow","m3/h","Num","R","A2"]
[null,null,"药剂计量箱容积","ChemicalTankCap","m3","Num","R","A2"]
[null,null,"药剂计量泵流量","ChemicalPumpFlow","m3/h","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","WaterFlow","m3/h","Inst","R","L"]
[null,null,"工作水温","WaterTemp","℃","Inst","R","L"]
[null,null,"工作压力","WaterPress","MPa","Inst","R","L"]
[null,null,"加药量","ChemicalFeed","mg/m3","Inst","M","L"]
[null,null,"药剂余量","ChemicalRemain","g","Inst","M","L"]
[null,null,"累计处理水量","AccWaterVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CCSD供冷软化水装置","index":15,"n_rows":38,"n_cols":10,"rows_kept":38,"cut":false,"hidden":false,"merged":[[37,0,37,1],[18,0,35,1],[2,0,17,1],[0,0,0,9],[1,0,1,1],[36,0,36,1]]}
["软化水装置"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定水流量","RatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"周期制水量","PeriodWaterVolume","m3","Num","M","A2",null,"Q=V×E/（I原水－I出水）"]
[null,null,"控制类型","CtrlType",null,"Enum","R","D1","1. 手动型 2. 国产组合自动型 3. 进口全自动型 4. 分立阀全自动型 99. 其他"]
[null,null,"功能类型","FuncType",null,"Enum","M","D1","1. 采暖补水 2. 冷却补水 99. 其他"]
[null,null,"额定进水硬度","RatedWaterInHardness","mg/L","Num","R","A2"]
[null,null,"额定出水硬度","RatedWaterOutHardness","mg/L","Num","R","A2"]
[null,null,"额定耗水量","RatedWaterConsum","mL/m3","Num","R","A2",null,"水耗<产水量的2%　\n盐耗<100克/克当量"]
[null,null,"树脂体积用量","RatedResinConsum","mL/m3","Num","R","A2"]
[null,null,"树脂的工作交换容量","ResinExchangeCap","mg/L","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","WaterFlow","m3/h","Inst","R","L"]
[null,null,"工作水温","WaterTemp","℃","Inst","R","L"]
[null,null,"工作压力","WaterPress","MPa","Inst","R","L"]
[null,null,"进水硬度","WaterInHardness","mg/L","Inst","R","L"]
[null,null,"出水硬度","WaterOutHardness","mg/L","Inst","R","L"]
[null,null,"累计处理水量","AccWaterVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CCTU供冷全程水处理仪","index":16,"n_rows":38,"n_cols":10,"rows_kept":38,"cut":false,"hidden":false,"merged":[[37,0,37,1],[15,0,35,1],[0,0,0,9],[1,0,1,1],[2,0,14,1],[36,0,36,1]]}
["全程水处理仪"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定水流量","RatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"功能类型","FuncType",null,"MEnum","M","D2","1. 防垢 2. 除垢 3. 杀菌 4. 灭藻 5. 防腐 6. 超净过滤 99. 其他 （多选）"]
[null,null,"安全绝缘电压","InsulationU","V","Num","R","A2",null,"瞬时电压最高值"]
[null,null,"防垢、除垢率","RatedAntiscaleRatio","%","Num","R","A2",null,"原理：电磁场 超声波"]
[null,null,"杀菌灭藻率","RatedSterilizeRaio","%","Num","R","A2",null,"原理：电磁场 超声波"]
[null,null,"过滤效率","RatedFilterRatio","%","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","WaterFlow","m3/h","Inst","R","L"]
[null,null,"工作水温","WaterTemp","℃","Inst","R","L"]
[null,null,"进口水压","WaterInPress","MPa","Inst","M","L"]
[null,null,"出口水压","WaterOutPress","MPa","Inst","M","L"]
[null,null,"出水水质硬度","WaterOutHardness","mg/L","Inst","R","L",null,"以CaCO3计"]
[null,null,"出水PH值","WaterOutPH",null,"Inst","R","L",null,"水处理质量的指标"]
[null,null,"出水余氯","WaterOutCl ",null,"Inst","R","L",null,"水处理质量的指标"]
[null,null,"出水溶解性固体","WaterOutDissolvedSolid",null,"Inst","R","L",null,"水处理质量的指标"]
[null,null,"累计处理水量","AccWaterVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CCST蓄冷热槽","index":17,"n_rows":37,"n_cols":10,"rows_kept":37,"cut":false,"hidden":false,"merged":[[35,0,35,1],[36,0,36,1],[33,1,34,1],[0,0,0,9],[1,0,1,1],[17,0,34,0],[17,1,32,1],[2,0,16,1]]}
["蓄冷热槽"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"功能类型","FuncType",null,"MEnum","S","D2","1. 蓄冷 2. 蓄热 99. 其他 （可多选）"]
[null,null,"槽长度","TankLength","m","Num","R","A2"]
[null,null,"槽宽度","TankWidth","m","Num","R","A2"]
[null,null,"槽高度","TankHeight","m","Num","R","A2"]
[null,null,"槽容积","TankVolume","m3","Num","M","A2"]
[null,null,"最大蓄冷量","TotCoolStore","kWh","Num","M","A2",null,"蓄冷"]
[null,null,"蓄冰形状","IceShapeType",null,"Enum","R","D1","1. 冰球 2. 凹面冰球 3. 蕊心冰球 4. 冰板 99. 其他","冰蓄冷"]
[null,null,"制冰率","IcingRate","%","Num","R","A2",null,"冰蓄冷"]
[null,null,"融冰率","DeicingRate","%","Num","R","A2",null,"冰蓄冷"]
[null,null,"管内乙二醇容积","GlycolCap","m3","Num","R","A2",null,"冰蓄冷"]
[null,null,"额定冷水温度","RatedColdWaterTemp","℃","Num","M","A2",null,"水蓄冷"]
[null,null,"最大蓄热量","MaxHeatStore","kWh","Num","M","A2",null,"蓄热"]
[null,null,"额定热水温度","RatedHotWaterTemp","℃","Num","M","A2",null,"蓄热"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"瞬时蓄冷量","CoolStoreP","kW","Inst","M","L",null,"蓄冷"]
[null,null,"瞬时放冷量","CoolReleaseP","kW","Inst","M","L",null,"蓄冷"]
[null,null,"蓄冰比例","IceRatio","%","Inst","R","L",null,"冰蓄冷"]
[null,null,"冷水温度","ColdWaterTemp","℃","Inst","M","L",null,"水蓄冷"]
[null,null,"瞬时蓄热量","HeatStoreP","kW","Inst","M","L",null,"蓄热"]
[null,null,"瞬时放热量","HeatReleaseP","kW","Inst","M","L",null,"蓄热"]
[null,null,"热水温度","HotWaterTemp","℃","Inst","M","L",null,"蓄热"]
[null,null,"累计蓄冷量","AccCoolStore","kWh","Acc","R","M",null,"蓄冷"]
[null,null,"累计放冷量","AccCoolRelease","kWh","Acc","R","M",null,"蓄冷"]
[null,null,"累计蓄热量","AccHeatStore","kWh","Acc","R","M",null,"蓄热"]
[null,null,"累计放热量","AccHeatRelease","kWh","Acc","R","M",null,"蓄热"]
[null,"瞬时指标","蓄冷效率","CoolStoreEff","%","Inst","R","M",null,"蓄冷"]
[null,null,"蓄热效率","HeatStoreEff","%","Inst","R","M",null,"蓄热"]
["设定参数"]
["报警消息"]

{"sheet":"CCDB供冷分水器","index":18,"n_rows":27,"n_cols":10,"rows_kept":27,"cut":false,"hidden":false,"merged":[[26,0,26,1],[0,0,0,9],[1,0,1,1],[13,0,24,1],[25,0,25,1],[2,0,12,1]]}
["分集水器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"总管数量","MainPipeNum","个","Num","S","A2"]
[null,null,"总管直径","MainPipeDN","mm","Num","R","A2"]
[null,null,"分管数量","BranchPipeNum","个","Num","S","A2"]
[null,null,"分管直径","BranchPipeDN","mm","Num","R","A2"]
[null,null,"材料类型","MaterialType",null,"Enum","R","D1","1. 钢板 2. 黄铜 3. PP/PE 99. 其他"]
[null,null,"是否有排气阀","isAirReleaseValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有泄水阀","isWaterEscapeValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有旁通管","isBypassPipe",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"总管阀门开度","MainPipeValveOpening","%","Inst","R","L"]
[null,null,"总管流量","MainPipeFlow","m3/h","Inst","M","L"]
[null,null,"总管温度","MainPipeTemp","℃","Inst","M","L"]
[null,null,"总管压力","MainPipePress","MPa","Inst","M","L"]
[null,null,"分管阀门开度","BranchPipeValveOpening","%","Insts","R","L"]
[null,null,"分管流量","BranchPipeFlow","m3/h","Insts","M","L"]
[null,null,"分管温度","BranchPipeTemp","℃","Insts","M","L"]
[null,null,"分管压力","BranchPipePress","MPa","Insts","M","L"]
[null,null,"旁通管阀门开度","BypassPipeValveOpening","%","Inst","M","L"]
[null,null,"旁通管流量","BypassPipeFlow","m3/h","Inst","R","L"]
[null,null,"旁通管温度","BypassPipeTemp","℃","Inst","R","L"]
[null,null,"旁通管压力","BypassPipePress","MPa","Inst","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"CCCL供冷集水器","index":19,"n_rows":27,"n_cols":10,"rows_kept":27,"cut":false,"hidden":false,"merged":[[26,0,26,1],[1,0,1,1],[0,0,0,9],[13,0,24,1],[25,0,25,1],[2,0,12,1]]}
["分集水器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"总管数量","MainPipeNum","个","Num","S","A2"]
[null,null,"总管直径","MainPipeDN","mm","Num","R","A2"]
[null,null,"分管数量","BranchPipeNum","个","Num","S","A2"]
[null,null,"分管直径","BranchPipeDN","mm","Num","R","A2"]
[null,null,"材料类型","MaterialType",null,"Enum","R","D1","1. 钢板 2. 黄铜 3. PP/PE 99. 其他"]
[null,null,"是否有排气阀","isAirReleaseValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有泄水阀","isWaterEscapeValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有旁通管","isBypassPipe",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"总管阀门开度","MainPipeValveOpening","%","Inst","R","L"]
[null,null,"总管流量","MainPipeFlow","m3/h","Inst","M","L"]
[null,null,"总管温度","MainPipeTemp","℃","Inst","M","L"]
[null,null,"总管压力","MainPipePress","MPa","Inst","M","L"]
[null,null,"分管阀门开度","BranchPipeValveOpening","%","Insts","R","L"]
[null,null,"分管流量","BranchPipeFlow","m3/h","Insts","M","L"]
[null,null,"分管温度","BranchPipeTemp","℃","Insts","M","L"]
[null,null,"分管压力","BranchPipePress","MPa","Insts","M","L"]
[null,null,"旁通管阀门开度","BypassPipeValveOpening","%","Inst","M","L"]
[null,null,"旁通管流量","BypassPipeFlow","m3/h","Inst","R","L"]
[null,null,"旁通管温度","BypassPipeTemp","℃","Inst","R","L"]
[null,null,"旁通管压力","BypassPipePress","MPa","Inst","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"CCWT供冷水箱","index":20,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[38,0,39,1],[26,0,36,1],[37,0,37,1],[0,0,0,9],[1,0,1,1],[2,0,25,0],[2,1,19,1],[20,1,22,1],[23,1,25,1]]}
["水箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","内胆","水箱长度","TankLength","m","Num","R","A2"]
[null,null,"水箱宽度","TankWidth","m","Num","R","A2"]
[null,null,"水箱高度","TankHeight","m","Num","R","A2"]
[null,null,"水箱容积","TankCap","m3","Num","S","A2"]
[null,null,"内胆材质","LiningMaterial",null,"Enum","R","D1","1. 不锈钢 2. 搪瓷 3. 塑料 4. 复合材料 99. 其他"]
[null,null,"最大承压","MaxPress","MPa","Num","M","A2"]
[null,null,"底板厚度","BottomBoardThick","mm","Num","R","A2"]
[null,null,"侧板厚度","SideBoardThick","mm","Num","R","A2"]
[null,null,"顶板厚度","TopBoardThick","mm","Num","R","A2"]
[null,null,"进水口截面积","InCrossArea","m2","Num","R","A2"]
[null,null,"出水口截面积","OutCrossArea","m2","Num","R","A2"]
[null,null,"溢流口截面积","OverflowCrossArea","m2","Num","R","A2"]
[null,null,"排污口截面积","SewageCrossArea","m2","Num","R","A2"]
[null,null,"人孔宽度","ManholeWidth","m","Num","R","A2"]
[null,null,"人孔高度","ManholeHeight","m","Num","R","A2"]
[null,null,"内外爬梯高度","LadderHeight","m","Num","R","A2"]
[null,null,"额定水温","RatedWaterTemp","℃","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,"保温层","是否有保温层","isInsulation",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"保温层材料","InsulationMaterial",null,"Enum","R","D1","1. 岩棉 2. 玻璃棉 3. 聚氨酯 4. 聚苯乙烯 5. 酚醛泡沫 99. 其他"]
[null,null,"保温层厚度","InsulationThick","mm","Num","R","A2"]
[null,"外壳","是否有外壳","isShield",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"外壳材质","ShieldMaterial ",null,"Enum","R","D1","1. 不锈钢 2. 塑料 99. 其他"]
[null,null,"外壳抗压强度","ShieldCompressiveStrength","MPa","Num","R","A2"]
["运行参数",null,"水箱水位","TankWaterLev","m","Inst","S","L"]
[null,null,"水箱水量","TankWaterVolume","m3","Inst","R","L"]
[null,null,"水箱水温","TankWaterTemp","℃","Inst","M","L"]
[null,null,"进水流量","WaterInFlow","m3/h","Inst","R","L"]
[null,null,"出水流量","WaterOutFlow","m3/h","Inst","R","L"]
[null,null,"溢流流量","OverflowFlow","m3/h","Inst","R","L"]
[null,null,"排污流量","SewageFlow","m3/h","Inst","R","L"]
[null,null,"进水温度","WaterInTemp","℃","Inst","R","L"]
[null,null,"进水口压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","R","L"]
[null,null,"出水口压力","WaterOutPress","MPa","Inst","R","L"]
["设定参数"]
["报警消息",null,"高液位报警","HighLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"低液位报警","LowLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]