{"text_format":"2","workbook":"xlsx","n_sheets":16,"sheets":["CHCB供热燃煤锅炉","CHFB供热燃油锅炉","CHGB供热燃气锅炉","CHEB供热电锅炉","CHHP供热水泵","CHFP供热补水泵","CHCF供热定压补水装置","CHHE供热换热器","CHVD供热真空脱气机","CHCD供热水加药装置","CHSD供热软化水装置","CHTU供热全程水处理仪","CHDB供热分水器","CHCL供热集水器","CHWT供热水箱","CHBF生物质炊暖炉"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"CHCB供热燃煤锅炉","index":0,"n_rows":66,"n_cols":10,"rows_kept":66,"cut":false,"hidden":false,"merged":[[35,1,53,1],[54,1,55,1],[56,1,61,1],[35,0,61,0],[64,0,65,1],[62,0,63,1],[0,0,0,9],[1,0,1,1],[2,0,34,0],[25,1,30,1],[31,1,34,1],[19,1,21,1],[22,1,24,1],[2,1,18,1]]}
["燃煤锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"燃煤类型","CoalType",null,"MEnum","R","D2","1. 无烟煤 2. 贫煤 3. 贫瘦煤 4. 瘦煤 5. 焦煤 6. 肥煤 7. 1/3焦煤 8. 气肥煤 9. 气煤 10. 1/2中粘煤 11. 不粘煤 12. 长焰煤 13. 褐煤 99. 其他 （可多选）"]
[null,null,"燃烧方式","BurnType",null,"Enum","M","D1","1. 层燃炉 2. 室燃炉 3. 旋风炉 4. 沸腾燃烧炉 99. 其他"]
[null,null,"除渣方式","DeSlagType",null,"Enum","R","D1","1. 固态除渣炉 2. 液态除渣炉 99. 其他"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定输入燃煤量","RatedCoalConsum","kg/h","Num","S","A2"]
[null,null,"额定工作压力","RatedPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","R","A2",null,"排去的污水量"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"烟气余热\n回收装置","烟气余热回收方式","HeatRecoveryType",null,"Enum","M","D1","1. 预热工件  2. 预热空气  3. 余热回收器（气-水） 4. 余热回收器（气-气）  5. 余热氨水吸收制冷 99. 其他"]
[null,null,"烟气余热回收换热器形式","RecoveryHeatExchangerType",null,"Enum","R","D1","1. 管式 2. 圆筒辐射式 3. 铸铁块状 99. 其他"]
[null,null,"烟气余热回收额定换热量","RatedRecoveryHeatTrans","kW","Num","M","A2"]
[null,null,"烟气余热回收理论换热效率","RatedRecoveryHeatTransEff","%","Num","R","A2"]
[null,null,"烟气余热回收最高工作温度","RecoveryMaxWorkTemp","℃","Num","R","A2"]
[null,null,"烟气余热回收最高工作压力","RecoveryMaxWorkPress","MPa","Num","R","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","M","L"]
[null,null,"燃煤量","CoalConsumP","kg/h","Inst","R","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水锅炉"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"蒸汽压力","VaporOutPress","MPa","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"吸气温度","InAirTemp","℃","Inst","R","L"]
[null,null,"排烟温度","ExhaustSmokeTemp","℃","Inst","M","L"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","M","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","M","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,null,"余热回收效率","HeatRecoveryEff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计燃煤量","AccCoalConsum","kg","Acc","R","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息",null,"排烟温度过高报警","ExhaustSmokeOverTempAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"燃烧器故障报警","BurnerErrorAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CHFB供热燃油锅炉","index":1,"n_rows":66,"n_cols":10,"rows_kept":66,"cut":false,"hidden":false,"merged":[[64,0,65,1],[0,0,0,9],[1,0,1,1],[2,0,32,0],[23,1,28,1],[29,1,32,1],[17,1,19,1],[20,1,22,1],[2,1,16,1],[33,1,53,1],[56,1,61,1],[54,1,55,1],[33,0,61,0],[62,0,63,1]]}
["燃油锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"燃油类型","FuelType",null,"Enum","S","D1","1. 柴油 2. 煤油 3. 重油 99. 其他"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定输入燃油量","RatedFuelConsum","L/h","Num","S","A2"]
[null,null,"额定工作压力","RatedWorkPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","R","A2",null,"排去的污水量"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporOutPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"烟气余热\n回收装置","烟气余热回收方式","HeatRecoveryType",null,"Enum","M","D1","1. 预热工件  2. 预热空气  3. 余热回收器（气-水） 4. 余热回收器（气-气）  5. 余热氨水吸收制冷 99. 其他"]
[null,null,"烟气余热回收换热器形式","RecoveryHeatExchangerType",null,"Enum","R","D1","1. 管式 2. 圆筒辐射式 3. 铸铁块状 99. 其他"]
[null,null,"烟气余热回收额定换热量","RatedRecoveryHeatTrans","kW","Num","M","A2"]
[null,null,"烟气余热回收理论换热效率","RatedRecoveryHeatTransEff","%","Num","R","A2"]
[null,null,"烟气余热回收最高工作温度","RecoveryMaxWorkTemp","℃","Num","R","A2"]
[null,null,"烟气余热回收最高工作压力","RecoveryMaxWorkPress","MPa","Num","R","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","M","L"]
[null,null,"燃油量","FuelConsumP","L/h","Inst","M","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水锅炉"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"蒸汽压力","VaporOutPress","MPa","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"吸气温度","InAirTemp","℃","Inst","R","L"]
[null,null,"排烟温度","ExhaustSmokeTemp","℃","Inst","M","L"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","M","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","M","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,null,"燃油进口压力","FuelInPress","MPa","Inst","R","L"]
[null,null,"燃油阀门开度","FuelValveOpening","%","Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,null,"余热回收效率","HeatRecoveryEff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计燃油量","AccCoalConsum","L","Acc","M","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息",null,"排烟温度过高报警","ExhaustSmokeOverTempAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"燃烧器故障报警","BurnerErrorAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CHGB供热燃气锅炉","index":2,"n_rows":66,"n_cols":10,"rows_kept":66,"cut":false,"hidden":false,"merged":[[64,0,65,1],[0,0,0,9],[1,0,1,1],[2,0,32,0],[33,0,61,0],[33,1,53,1],[54,1,55,1],[56,1,61,1],[23,1,28,1],[29,1,32,1],[17,1,19,1],[20,1,22,1],[2,1,16,1],[62,0,63,1]]}
["燃气锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"燃气类型","GasType",null,"Enum","S","D1","1. 天然气 2. 液化石油气 3. 沼气 4. 城市煤气 99. 其他"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定输入燃气量","RatedGasConsum","m3/h","Num","S","A2"]
[null,null,"额定工作压力","RatedWorkPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","R","A2",null,"排去的污水量"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporOutPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"烟气余热\n回收装置","烟气余热回收方式","HeatRecoveryType",null,"Enum","M","D1","1. 预热工件  2. 预热空气  3. 余热回收器（气-水） 4. 余热回收器（气-气）  5. 余热氨水吸收制冷 99. 其他"]
[null,null,"烟气余热回收换热器形式","RecoveryHeatExchangerType",null,"Enum","R","D1","1. 管式 2. 圆筒辐射式 3. 铸铁块状 99. 其他"]
[null,null,"烟气余热回收额定换热量","RatedRecoveryHeatTrans","kW","Num","M","A2"]
[null,null,"烟气余热回收理论换热效率","RatedRecoveryHeatTransEff","%","Num","R","A2"]
[null,null,"烟气余热回收最高工作温度","RecoveryMaxWorkTemp","℃","Num","R","A2"]
[null,null,"烟气余热回收最高工作压力","RecoveryMaxWorkPress","MPa","Num","R","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","M","L"]
[null,null,"燃气量","GasConsumP","m3/h","Inst","M","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水系统"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水系统"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽系统"]
[null,null,"蒸汽压力","VaporOutPress","MPa","Inst","S","L",null,"蒸汽系统"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"吸气温度","InAirTemp","℃","Inst","R","L"]
[null,null,"排烟温度","ExhaustSmokeTemp","℃","Inst","M","L"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","M","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","M","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,null,"燃气进口压力","GasInPress","MPa","Inst","R","L"]
[null,null,"燃气阀门开度","GasValveOpening","%","Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,null,"余热回收效率","HeatRecoveryEff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计燃气量","AccGasConsum","m3","Acc","M","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息",null,"排烟温度过高报警","ExhaustSmokeOverTempAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"燃烧器故障报警","BurnerErrorAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"CHEB供热电锅炉","index":3,"n_rows":65,"n_cols":10,"rows_kept":65,"cut":false,"hidden":false,"merged":[[64,0,64,1],[22,1,24,1],[25,1,27,1],[0,0,0,9],[1,0,1,1],[2,0,31,0],[28,1,31,1],[2,1,21,1],[32,0,61,0],[32,1,54,1],[56,1,61,1],[62,0,63,1]]}
["电锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定耗电功率","RatedElecConsumP","kW","Num","S","A2"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定工作压力","RatedWorkPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","M","A2",null,"排去的污水量"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"绝缘等级","InsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporOutPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","S","L"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","S","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水锅炉"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"蒸汽压力","VaporPress","MPa","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","R","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","R","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息"]

{"sheet":"CHHP供热水泵","index":4,"n_rows":77,"n_cols":10,"rows_kept":77,"cut":false,"hidden":false,"merged":[[67,1,72,1],[73,0,75,1],[76,0,76,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息"]

{"sheet":"CHFP供热补水泵","index":5,"n_rows":77,"n_cols":10,"rows_kept":77,"cut":false,"hidden":false,"merged":[[73,0,75,1],[76,0,76,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[67,1,72,1],[1,0,1,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S",null,"0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S",null,"1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息"]

{"sheet":"CHCF供热定压补水装置","index":6,"n_rows":23,"n_cols":10,"rows_kept":23,"cut":false,"hidden":false,"merged":[[22,0,22,1],[1,0,1,1],[0,0,0,9],[11,0,20,1],[21,0,21,1],[2,0,10,1]]}
["定压补水装置"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"最大工作压力","MaxWorkPress","MPa","Num","M","A2"]
[null,null,"定压精度","ConstantPressAccuracy","MPa","Num","R","A2"]
[null,null,"给水压力","SupplyWaterPress","MPa","Num","M","A2"]
[null,null,"总容积","TotCap","m3","Num","M","A2"]
[null,null,"调节容积","AdjustCap","m3","Num","R","A2"]
[null,null,"供水能力范围","SupplyWaterRange","m3/h","Num","R","A6"]
[null,null,"排气模式","ExhaustType",null,"Enum","R","D1","1. 常压隔膜罐排气 2. 真空排气 99. 其他"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"水箱水量","TankVolume","m3","Inst","M","L"]
[null,null,"水箱压力","TankPress","MPa","Inst","M","L"]
[null,null,"补水状态","FillingStatus",null,"Boolv","M","L","0. 未补水 1. 补水"]
[null,null,"日补水量","DayFilling","m3","Inst","R","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CHHE供热换热器","index":7,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":false,"merged":[[0,0,0,9],[42,0,42,1],[43,0,43,1],[1,0,1,1],[39,1,41,1],[2,0,16,1],[17,0,41,0],[17,1,38,1]]}
["换热器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"换热介质类型","MediumType",null,"Enum","S","D1","1. 水-水换热 2. 水-汽换热 99. 其他"]
[null,null,"结构类型","StructureType",null,"Enum","M","D1","1. 夹套式换热器 2. 蛇管式换热器 3. 套管式换热器 4. 列管式换热器 5. 板片式换热器 6. 非金属换热器 99. 其他"]
[null,null,"设计换热量","DesignHeatTrans","kW","Num","M","A2"]
[null,null,"换热面积","HeatTransArea","m2","Num","R","A2"]
[null,null,"高温侧设计水流量","DesignHighFlow","m3/h","Num","R","A2"]
[null,null,"高温侧设计进水温度","DesignHighInTemp","℃","Num","R","A2"]
[null,null,"高温侧设计出水温度","DesignHighOutTemp","℃","Num","R","A2"]
[null,null,"高温侧设计供蒸汽压力","DesignHighVaporPress","MPa","Num","R","A2",null,"水-汽换热时"]
[null,null,"高温侧设计供蒸汽流量","DesignHighVaporFlow","t/h","Num","R","A2",null,"水-汽换热时"]
[null,null,"低温侧设计水流量","DesignLowFlow","m3/h","Num","R","A2"]
[null,null,"低温侧设计进水温度","DesignLowInTemp","℃","Num","R","A2"]
[null,null,"低温侧设计出水温度","DesignLowOutTemp","℃","Num","R","A2"]
[null,null,"传热系数","HeatTransCoeff","W/(m2K)","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"换热功率","HeatTransP","kW","Inst","R","L"]
[null,null,"高温侧进水温度","HighInTemp","℃","Inst","S","L"]
[null,null,"高温侧出水温度","HighOutTemp","℃","Inst","S","L"]
[null,null,"高温侧水阀开度","HighValveOpening","%","Inst","R","L"]
[null,null,"高温侧瞬时流量","HighFlow","m3/h","Inst","M","L"]
[null,null,"高温侧进水压力","HighInPress","MPa","Inst","R","L"]
[null,null,"高温侧出水压力","HighOutPress","MPa","Inst","R","L"]
[null,null,"高温侧供蒸汽压力","HighVaporPress","MPa","Inst","S","L",null,"水-汽换热时"]
[null,null,"高温侧凝水温度","HighCondenseWaterTemp","℃","Inst","M","L",null,"水-汽换热时"]
[null,null,"高温侧蒸汽阀开度","HighVaporValveOpening","%","Inst","R","L",null,"水-汽换热时"]
[null,null,"高温侧瞬时蒸汽流量","HighVaporFlow","t/h","Inst","M","L",null,"水-汽换热时"]
[null,null,"低温侧进水温度","LowInTemp","℃","Inst","S","L"]
[null,null,"低温侧出水温度","LowOutTemp","℃","Inst","S","L"]
[null,null,"低温侧水阀状态","LowValveOpening","%","Inst","R","L"]
[null,null,"低温侧瞬时流量","LowFlow","m3/h","Inst","M","L"]
[null,null,"低温侧进水压力","LowInPress","MPa","Inst","R","L"]
[null,null,"低温侧出水压力","LowOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","换热器高温侧阻力","HighResistance","MPa","Inst","R","M"]
[null,null,"换热器低温侧阻力","LowResistance","MPa","Inst","R","M"]
[null,null,"换热效率","HeatTransEff","%","Inst","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CHVD供热真空脱气机","index":8,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":false,"merged":[[43,0,43,1],[1,0,1,1],[0,0,0,9],[2,0,19,1],[20,0,41,0],[20,1,34,1],[35,1,36,1],[37,1,41,1],[42,0,42,1]]}
["真空脱气机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"处理能力","ProcessCapacity","m3/h","Num","M","A2"]
[null,null,"额定游离气体析除率","RatedFreeGasRemoveRatio","%","Num","M","A2"]
[null,null,"额定溶解气体析除率","RatedDissolvedGasRemoveRatio","%","Num","M","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","MediumFlow","m3/h","Inst","M","L"]
[null,null,"工作水温","MediumTemp","℃","Inst","R","L"]
[null,null,"工作压力","MediumPress","MPa","Inst","R","L"]
[null,null,"进水游离气体含量","InFreeGas","mL/m3","Inst","R","L"]
[null,null,"出水游离气体含量","OutFreeGas","mL/m3","Inst","R","L"]
[null,null,"进水溶解气体含量","InDissolvedGas","mL/m3","Inst","R","L"]
[null,null,"出水溶解气体含量","OutDissolvedGas","mL/m3","Inst","R","L"]
[null,"瞬时指标","游离气体析除率","FreeGasRemoveRatio","h","Inst","R","M"]
[null,null,"溶解气体析除率","DissolvedGasRemoveRatio","h","Inst","R","M"]
[null,"累计指标","累计处理水量","AccMediumVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CHCD供热水加药装置","index":9,"n_rows":37,"n_cols":10,"rows_kept":37,"cut":false,"hidden":false,"merged":[[36,0,36,1],[1,0,1,1],[0,0,0,9],[2,0,16,1],[17,0,34,1],[35,0,35,1]]}
["水加药装置"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定水流量","RatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"加药方式","ChemicalFeedType",null,"Enum","M","D1","1. 人工投料 2. 自动投料 99. 其他"]
[null,null,"配药用水压力","RatedChemicalWaterPress","MPa","Num","R","A2"]
[null,null,"配药用水温度","RatedChemicalWaterTemp","℃","Num","R","A2"]
[null,null,"稳定剂计量箱容积","StabilizerTankCap","m3","Num","R","A2"]
[null,null,"稳定剂计量泵流量","StabilizerPumpFlow","m3/h","Num","R","A2"]
[null,null,"药剂计量箱容积","ChemicalTankCap","m3","Num","R","A2"]
[null,null,"药剂计量泵流量","ChemicalPumpFlow","m3/h","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","WaterFlow","m3/h","Inst","R","L"]
[null,null,"工作水温","WaterTemp","℃","Inst","R","L"]
[null,null,"工作压力","WaterPress","MPa","Inst","R","L"]
[null,null,"加药量","ChemicalFeed","mg/m3","Inst","M","L"]
[null,null,"药剂余量","ChemicalRemain","g","Inst","M","L"]
[null,null,"累计处理水量","AccWaterVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CHSD供热软化水装置","index":10,"n_rows":38,"n_cols":10,"rows_kept":38,"cut":false,"hidden":false,"merged":[[37,0,37,1],[1,0,1,1],[0,0,0,9],[2,0,17,1],[18,0,35,1],[36,0,36,1]]}
["软化水装置"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定水流量","RatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"周期制水量","PeriodWaterVolume","m3","Num","M","A2",null,"Q=V×E/（I原水－I出水）"]
[null,null,"控制类型","CtrlType",null,"Enum","R","D1","1. 手动型 2. 国产组合自动型 3. 进口全自动型 4. 分立阀全自动型 99. 其他"]
[null,null,"功能类型","FuncType",null,"Enum","M","D1","1. 采暖补水 2. 冷却补水 99. 其他"]
[null,null,"额定进水硬度","RatedWaterInHardness","mg/L","Num","R","A2"]
[null,null,"额定出水硬度","RatedWaterOutHardness","mg/L","Num","R","A2"]
[null,null,"额定耗水量","RatedWaterConsum","mL/m3","Num","R","A2",null,"水耗<产水量的2%　\n盐耗<100克/克当量"]
[null,null,"树脂体积用量","RatedResinConsum","mL/m3","Num","R","A2"]
[null,null,"树脂的工作交换容量","ResinExchangeCap","mg/L","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","WaterFlow","m3/h","Inst","R","L"]
[null,null,"工作水温","WaterTemp","℃","Inst","R","L"]
[null,null,"工作压力","WaterPress","MPa","Inst","R","L"]
[null,null,"进水硬度","WaterInHardness","mg/L","Inst","R","L"]
[null,null,"出水硬度","WaterOutHardness","mg/L","Inst","R","L"]
[null,null,"累计处理水量","AccWaterVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CHTU供热全程水处理仪","index":11,"n_rows":38,"n_cols":10,"rows_kept":38,"cut":false,"hidden":false,"merged":[[37,0,37,1],[1,0,1,1],[0,0,0,9],[2,0,14,1],[15,0,35,1],[36,0,36,1]]}
["全程水处理仪"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定水流量","RatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"功能类型","FuncType",null,"MEnum","M","D2","1. 防垢 2. 除垢 3. 杀菌 4. 灭藻 5. 防腐 6. 超净过滤 99. 其他 （多选）"]
[null,null,"安全绝缘电压","InsulationU","V","Num","R","A2",null,"瞬时电压最高值"]
[null,null,"防垢、除垢率","RatedAntiscaleRatio","%","Num","R","A2",null,"原理：电磁场 超声波"]
[null,null,"杀菌灭藻率","RatedSterilizeRaio","%","Num","R","A2",null,"原理：电磁场 超声波"]
[null,null,"过滤效率","RatedFilterRatio","%","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"处理水流量","WaterFlow","m3/h","Inst","R","L"]
[null,null,"工作水温","WaterTemp","℃","Inst","R","L"]
[null,null,"进口水压","WaterInPress","MPa","Inst","M","L"]
[null,null,"出口水压","WaterOutPress","MPa","Inst","M","L"]
[null,null,"出水水质硬度","WaterOutHardness","mg/L","Inst","R","L",null,"以CaCO3计"]
[null,null,"出水PH值","WaterOutPH",null,"Inst","R","L",null,"水处理质量的指标"]
[null,null,"出水余氯","WaterOutCl ",null,"Inst","R","L",null,"水处理质量的指标"]
[null,null,"出水溶解性固体","WaterOutDissolvedSolid",null,"Inst","R","L",null,"水处理质量的指标"]
[null,null,"累计处理水量","AccWaterVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"CHDB供热分水器","index":12,"n_rows":27,"n_cols":10,"rows_kept":27,"cut":false,"hidden":false,"merged":[[26,0,26,1],[1,0,1,1],[0,0,0,9],[13,0,24,1],[25,0,25,1],[2,0,12,1]]}
["分集水器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"总管数量","MainPipeNum","个","Num","S","A2"]
[null,null,"总管直径","MainPipeDN","mm","Num","R","A2"]
[null,null,"分管数量","BranchPipeNum","个","Num","S","A2"]
[null,null,"分管直径","BranchPipeDN","mm","Num","R","A2"]
[null,null,"材料类型","MaterialType",null,"Enum","R","D1","1. 钢板 2. 黄铜 3. PP/PE 99. 其他"]
[null,null,"是否有排气阀","isAirReleaseValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有泄水阀","isWaterEscapeValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有旁通管","isBypassPipe",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"总管阀门开度","MainPipeValveOpening","%","Inst","R","L"]
[null,null,"总管流量","MainPipeFlow","m3/h","Inst","M","L"]
[null,null,"总管温度","MainPipeTemp","℃","Inst","M","L"]
[null,null,"总管压力","MainPipePress","MPa","Inst","M","L"]
[null,null,"分管阀门开度","BranchPipeValveOpening","%","Insts","R","L"]
[null,null,"分管流量","BranchPipeFlow","m3/h","Insts","M","L"]
[null,null,"分管温度","BranchPipeTemp","℃","Insts","M","L"]
[null,null,"分管压力","BranchPipePress","MPa","Insts","M","L"]
[null,null,"旁通管阀门开度","BypassPipeValveOpening","%","Inst","M","L"]
[null,null,"旁通管流量","BypassPipeFlow","m3/h","Inst","R","L"]
[null,null,"旁通管温度","BypassPipeTemp","℃","Inst","R","L"]
[null,null,"旁通管压力","BypassPipePress","MPa","Inst","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"CHCL供热集水器","index":13,"n_rows":27,"n_cols":10,"rows_kept":27,"cut":false,"hidden":false,"merged":[[26,0,26,1],[1,0,1,1],[0,0,0,9],[13,0,24,1],[25,0,25,1],[2,0,12,1]]}
["分集水器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"总管数量","MainPipeNum","个","Num","S","A2"]
[null,null,"总管直径","MainPipeDN","mm","Num","R","A2"]
[null,null,"分管数量","BranchPipeNum","个","Num","S","A2"]
[null,null,"分管直径","BranchPipeDN","mm","Num","R","A2"]
[null,null,"材料类型","MaterialType",null,"Enum","R","D1","1. 钢板 2. 黄铜 3. PP/PE 99. 其他"]
[null,null,"是否有排气阀","isAirReleaseValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有泄水阀","isWaterEscapeValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有旁通管","isBypassPipe",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"总管阀门开度","MainPipeValveOpening","%","Inst","R","L"]
[null,null,"总管流量","MainPipeFlow","m3/h","Inst","M","L"]
[null,null,"总管温度","MainPipeTemp","℃","Inst","M","L"]
[null,null,"总管压力","MainPipePress","MPa","Inst","M","L"]
[null,null,"分管阀门开度","BranchPipeValveOpening","%","Insts","R","L"]
[null,null,"分管流量","BranchPipeFlow","m3/h","Insts","M","L"]
[null,null,"分管温度","BranchPipeTemp","℃","Insts","M","L"]
[null,null,"分管压力","BranchPipePress","MPa","Insts","M","L"]
[null,null,"旁通管阀门开度","BypassPipeValveOpening","%","Inst","M","L"]
[null,null,"旁通管流量","BypassPipeFlow","m3/h","Inst","R","L"]
[null,null,"旁通管温度","BypassPipeTemp","℃","Inst","R","L"]
[null,null,"旁通管压力","BypassPipePress","MPa","Inst","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"CHWT供热水箱","index":14,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[38,0,39,1],[26,0,36,1],[37,0,37,1],[1,0,1,1],[0,0,0,9],[2,0,25,0],[2,1,19,1],[20,1,22,1],[23,1,25,1]]}
["水箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","内胆","水箱长度","TankLength","m","Num","R","A2"]
[null,null,"水箱宽度","TankWidth","m","Num","R","A2"]
[null,null,"水箱高度","TankHeight","m","Num","R","A2"]
[null,null,"水箱容积","TankCap","m3","Num","S","A2"]
[null,null,"内胆材质","LiningMaterial",null,"Enum","R","D1","1. 不锈钢 2. 搪瓷 3. 塑料 4. 复合材料 99. 其他"]
[null,null,"最大承压","MaxPress","MPa","Num","M","A2"]
[null,null,"底板厚度","BottomBoardThick","mm","Num","R","A2"]
[null,null,"侧板厚度","SideBoardThick","mm","Num","R","A2"]
[null,null,"顶板厚度","TopBoardThick","mm","Num","R","A2"]
[null,null,"进水口截面积","InCrossArea","m2","Num","R","A2"]
[null,null,"出水口截面积","OutCrossArea","m2","Num","R","A2"]
[null,null,"溢流口截面积","OverflowCrossArea","m2","Num","R","A2"]
[null,null,"排污口截面积","SewageCrossArea","m2","Num","R","A2"]
[null,null,"人孔宽度","ManholeWidth","m","Num","R","A2"]
[null,null,"人孔高度","ManholeHeight","m","Num","R","A2"]
[null,null,"内外爬梯高度","LadderHeight","m","Num","R","A2"]
[null,null,"额定水温","RatedWaterTemp","℃","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,"保温层","是否有保温层","isInsulation",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"保温层材料","InsulationMaterial",null,"Enum","R","D1","1. 岩棉 2. 玻璃棉 3. 聚氨酯 4. 聚苯乙烯 5. 酚醛泡沫 99. 其他"]
[null,null,"保温层厚度","InsulationThick","mm","Num","R","A2"]
[null,"外壳","是否有外壳","isShield",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"外壳材质","ShieldMaterial ",null,"Enum","R","D1","1. 不锈钢 2. 塑料 99. 其他"]
[null,null,"外壳抗压强度","ShieldCompressiveStrength","MPa","Num","R","A2"]
["运行参数",null,"水箱水位","TankWaterLev","m","Inst","S","L"]
[null,null,"水箱水量","TankWaterVolume","m3","Inst","R","L"]
[null,null,"水箱水温","TankWaterTemp","℃","Inst","M","L"]
[null,null,"进水流量","WaterInFlow","m3/h","Inst","R","L"]
[null,null,"出水流量","WaterOutFlow","m3/h","Inst","R","L"]
[null,null,"溢流流量","OverflowFlow","m3/h","Inst","R","L"]
[null,null,"排污流量","SewageFlow","m3/h","Inst","R","L"]
[null,null,"进水温度","WaterInTemp","℃","Inst","R","L"]
[null,null,"进水口压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","R","L"]
[null,null,"出水口压力","WaterOutPress","MPa","Inst","R","L"]
["设定参数"]
["报警消息",null,"高液位报警","HighLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"低液位报警","LowLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]

{"sheet":"CHBF生物质炊暖炉","index":15,"n_rows":34,"n_cols":10,"rows_kept":34,"cut":false,"hidden":false,"merged":[[24,0,33,1],[0,0,0,9],[1,0,1,1],[2,0,3,1],[4,0,20,1],[21,0,23,1]]}
["生物质炊暖炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"控制器版本",null,null,"Str","M","B1"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"取暖模式状态","HeatingModeStatus",null,"Boolv","S","L","0. 关闭 1. 取暖"]
[null,null,"炊事模式状态","CookingModeStatus",null,"Boolv","S","L","0. 关闭 1. 炊事"]
[null,null,"环境温度","RoomTemp","℃","Inst","R","L"]
[null,null,"炉膛火焰温度","FurnaceFlameTemp","℃","Inst","R","L"]
[null,null,"排烟温度","ExhaustGasTemp","℃","Inst","R","L"]
[null,null,"出水温度","OutWaterTemp","℃","Inst","M","L"]
[null,null,"回水温度","InWaterTemp","℃","Inst","M","L"]
[null,null,"出水流量","OutWaterFlow","m3/h","Inst","M","L"]
[null,null,"锅炉负荷","BoilerLoad","kW","Inst","M","M",null,"进料机负荷"]
[null,null,"风机负荷","FanLoad","kW","Inst","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"累计炊事时间","AccCookingTime","h","Acc","R","M"]
["设定参数",null,"目标取暖水温","OutWaterTempSet","℃","Nump","S","L"]
[null,null,"目标环境温度","RoomTempSet","℃","Nump","S","L"]
[null,null,"热需求时间段","HeatingTimeSet",null,"Timeps","M","L"]
["报警消息",null,"报警状态","AlarmStatus",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"极限超温报警","OverTempLimitAlarm",null,"Boolp","S","L","0. 正常 1. 极限超温"]
[null,null,"高水温报警","HighWaterTempAlarm",null,"Boolp","S","L","0. 正常 1. 高水温"]
[null,null,"出回水温度安装错误报警","TempSensorAlarm",null,"Boolp","S","L","0. 正常 1. 传感器错误"]
[null,null,"排烟温度超高报警","ExhaustGasHighTempAlarm",null,"Boolp","S","L","0. 正常 1. 高烟温"]
[null,null,"能耗偏高报警","EComsumHighAlarm",null,"Boolp","S","L","0. 正常 1. 能耗高"]
[null,null,"防冻报警","FreezeProofAlarm",null,"Boolp","S","L","0. 正常 1. 防冻报警"]
[null,null,"冰冻报警","FreezeAlarm",null,"Boolp","S","L","0. 正常 1. 冰冻"]
[null,null,"燃料不足报警","FuelShortAlarm",null,"Boolp","S","L","0. 正常 1. 缺料"]
[null,null,"点火故障报警","FireFaultAlarm",null,"Boolp","S","L","0. 正常 1. 点火失败"]