{"text_format":"2","workbook":"xlsx","n_sheets":16,"sheets":["ATAH空调机组","ATFU新风机组","ATFC风机盘管","ATSA分体空调","ATVR变频多联机","ATVA变风量箱","ATFA地板空调器","ATIO空调风口","ATRD散热器","ATFH地板采暖设备","ATVI变频多联机室内机","ATVO变频多联机室外机","ATHD空调加湿器","ATMF空调消声器","ATPC空调静压箱","ATCA定风量箱"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"ATAH空调机组","index":0,"n_rows":226,"n_cols":10,"rows_kept":226,"cut":false,"hidden":false,"merged":[[221,0,225,1],[208,0,220,1],[2,1,27,1],[0,0,0,9],[1,0,1,1],[102,0,207,0],[2,0,101,0],[55,1,58,1],[85,1,87,1],[88,1,89,1],[102,1,186,1],[199,1,207,1],[43,1,54,1],[59,1,84,1],[28,1,42,1],[90,1,100,1],[187,1,198,1]]}
["空调机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"机组送风能力","SupplyCap","m3/h","Num","S","A2"]
[null,null,"设计机外余压","DesignExcessPress","Pa","Num","M","A2"]
[null,null,"夏季工况设计送风温度","SummerDesignSupplyAirTemp","℃","Num","M","A2"]
[null,null,"夏季工况设计送风相对湿度","SummerDesignSupplyAirRH","%RH","Num","M","A2"]
[null,null,"夏季工况设计送风量","SummerDesignSupplyAirFlow","m3/h","Num","M","A2"]
[null,null,"冬季工况设计送风温度","WinterDesignSupplyAirTemp","℃","Num","M","A2"]
[null,null,"冬季工况设计送风相对湿度","WinterDesignSupplyAirRH","%RH","Num","M","A2"]
[null,null,"冬季工况设计送风量","WinterDesignSupplyAirFlow","m3/h","Num","M","A2"]
[null,null,"空调箱内部截面长度","CrossLength","m","Num","R","A2"]
[null,null,"空调箱内部截面高度","CrossHeight","m","Num","R","A2"]
[null,null,"漏风率","LeakageRatio ","%","Num","R","A2"]
[null,null,"功能段连接关系","SectionConnect",null,"Topology","R","I"]
[null,null,"设计工况空调机组处理过程焓湿图","DesignIDGraph",null,"Attachment","R","F2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"新风段","有无新风段","isFreshAirSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"新风口长度","FreshAirInletLength","m","Num","R","A2"]
[null,null,"新风口高度","FreshAirInletHeight","m","Num","R","A2"]
[null,null,"设计最小新风量","MinFreshAirFlow","m3/h","Num","R","A2"]
[null,null,"设计最大新风量","MaxFreshAirFlow","m3/h","Num","R","A2"]
[null,null,"新风阀调节范围","FreshAirValveRange","%","Numr","M","A2"]
[null,null,"过滤方式","FreshAirFiltType",null,"Enum","R","D1","1. 无 2. 格栅 3. 初效滤网 99. 其他"]
[null,null,"过滤效率","RatedFreshAirFiltEff","%","Num","R","A2"]
[null,null,"是否有新风预热设备","isFreshAirPreheat",null,"Bool","M","E1","0. 无 1. 有","不包括热回收"]
[null,null,"新风预热最大功率","FreshAirPreheatMaxP","kW","Num","M","A2",null,"不包括热回收"]
[null,null,"新风热回收类型","FreshAirHeatRecoveryType",null,"Enum","M","D1","1. 无热回收 2. 板式 3. 转轮式 4. 热管式 5. 中间热媒式 6. 热泵式 99. 其他"]
[null,null,"夏季工况新风热回收显热效率","SummerDesignFreshAirHeatRecoverySensibleHeatEff","%","Num","R","A2"]
[null,null,"夏季工况新风热回收全热效率","SummerDesignFreshAirHeatRecoveryTotalHeatEff","%","Num","R","A2"]
[null,null,"冬季工况新风热回收显热效率","WinterDesignFreshAirHeatRecoverySensibleHeatEff","%","Num","R","A2"]
[null,null,"冬季工况新风热回收全热效率","WinterDesignFreshAirHeatRecoveryTotHeatEff","%","Num","R","A2"]
[null,"混风段","有无混风段","isMixSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"混风类型","MixType",null,"Enum","M","D1","1. 一次回风  2. 二次回风 99. 其他"]
[null,null,"夏季工况设计回风温度","SummerDesignReturnAirTemp","℃","Num","R","A2"]
[null,null,"夏季工况设计回风相对湿度","SummerDesignReturnAirRH","%RH","Num","R","A2"]
[null,null,"冬季工况设计回风温度","WinterDesignReturnAirTemp","℃","Num","R","A2"]
[null,null,"冬季工况设计回风相对湿度","WinterDesignReturnAirRH","%RH","Num","R","A2"]
[null,null,"夏季工况设计回风量","SummerDesignReturnAirFlow","m3/h","Num","R","A2",null,"一次回风系统"]
[null,null,"冬季工况设计回风量","WinterDesignReturnAirFlow","m3/h","Num","R","A2",null,"一次回风系统"]
[null,null,"夏季工况设计一次回风量","SummerDesignPrimaryReturnAirFlow","m3/h","Num","R","A2",null,"二次回风系统"]
[null,null,"夏季工况设计二次回风量","SummerDesignSecondaryReturnAirFlow","m3/h","Num","R","A2",null,"二次回风系统"]
[null,null,"冬季工况设计一次回风量","WinterDesignPrimaryReturnAirFlow","m3/h","Num","R","A2",null,"二次回风系统"]
[null,null,"冬季工况设计二次回风量","WinterDesignSecondaryReturnAirFlow","m3/h","Num","R","A2",null,"二次回风系统"]
[null,"过滤段","有无过滤段","isFiltSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"过滤段个数","FiltNum","个","Num","R","A2"]
[null,null,"过滤段类型","FiltType",null,"MEnum","R","D2","1. 初效过滤段 2. 中小过滤段 3. 亚高效过滤段 4. 高效过滤段 5. 活性炭过滤段 99. 其他 （可多选）"]
[null,null,"额定过滤效率","FilterRatedEff","%","Nums","R","A4"]
[null,"表冷段","有无表冷段","isCoolCoilSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"夏季工况额定空气进口温度","SummerDesignCoolCoilAirInTemp","℃","Num","R","A2"]
[null,null,"夏季工况额定空气进口相对湿度","SummerDesignCoolCoilAirInRH","%RH","Num","R","A2"]
[null,null,"夏季工况额定空气出口温度","SummerDesignCoolCoilAirOutTemp","℃","Num","R","A2"]
[null,null,"夏季工况额定空气出口相对湿度","SummerDesignCoolCoilAirOutRH","%RH","Num","R","A2"]
[null,null,"冬季工况额定空气进口温度","WinterDesignCoolCoilAirInTemp","℃","Num","R","A2"]
[null,null,"冬季工况额定空气进口相对湿度","WinterDesignCoolCoilAirInRH","%RH","Num","R","A2"]
[null,null,"冬季工况额定空气出口温度","WinterDesignCoolCoilAirOutTemp","℃","Num","R","A2"]
[null,null,"冬季工况额定空气出口相对湿度","WinterDesignCoolCoilAirOutRH","%RH","Num","R","A2"]
[null,null,"空气侧换热面积","CoolCoilHeatTransArea","m2","Num","R","A2"]
[null,null,"设计机器露点","RatedCoolCoilMachineDewdrop","%","Num","R","A2"]
[null,null,"夏季工况设计制冷量","SummerDesignCoolP","kW","Num","M","A2",null,"显热"]
[null,null,"夏季工况设计除湿量","SummerDesignDeD","g/h","Num","M","A2"]
[null,null,"冬季工况设计制冷量","WinterDesignCoolP","kW","Num","R","A2",null,"显热；若冬季需要制冷"]
[null,null,"冬季工况设计除湿量","WinterDesignDeD","g/h","Num","R","A2",null,"若冬季需要除湿"]
[null,null,"夏季工况设计冷水进口温度","SummerDesignChillWaterInTemp","℃","Num","R","A2"]
[null,null,"夏季工况设计冷水出口温度","SummerDesignChillWaterOutTemp","℃","Num","R","A2"]
[null,null,"夏季工况设计冷水流量","SummerDesignChillWaterFlow","m3/h","Num","R","A2"]
[null,null,"冬季工况设计冷水进口温度","WinterDesignChillWaterInTemp","℃","Num","R","A2",null,"若冬季需要制冷或除湿"]
[null,null,"冬季工况设计冷水出口温度","WinterDesignChillWaterOutTemp","℃","Num","R","A2",null,"若冬季需要制冷或除湿"]
[null,null,"冬季工况设计冷水流量","WinterDesignChillWaterFlow","m3/h","Num","R","A2",null,"若冬季需要制冷或除湿"]
[null,null,"有无热水加热功能","isHotWaterFunc",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"设计制热量","DesignHeatP","kW","Num","M","A2",null,"热水加热盘管"]
[null,null,"设计热水进口温度","DesignHotWaterInTemp","℃","Num","R","A2",null,"热水加热盘管"]
[null,null,"设计热水出口温度","DesignHotWaterOutTemp","℃","Num","R","A2",null,"热水加热盘管"]
[null,null,"设计热水流量","DesignHotWaterFlow","m3/h","Num","R","A2",null,"热水加热盘管"]
[null,"加湿段","有无加湿段","isDSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"加湿方式","Dtype",null,"Enum","R","D1","1. 湿膜式 2. 超声波式 3. 电热式 4. 高压喷雾式 5. 干蒸汽式 6. 离心式 99. 其他"]
[null,null,"最大加湿量","MaxD","g/h","Num","R","A2"]
[null,"再热段","有无再热段","isReheatSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"最大加热功率","MaxReheatP","kW","Num","R","A2"]
[null,"送风段","有无送风段","isSupplySection",null,"Enum","M","E1","0. 无 1. 有"]
[null,null,"风机类型","FanType",null,"Bool","S","D1","1. 离心风机 2. 轴流风机 3. 贯流风机 99. 其他"]
[null,null,"风机有无变频功能","isFanVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"风机额定频率","RatedFanFreq","Hz","Num","M","A2"]
[null,null,"风机额定风量","RatedFanFlow","m3/h","Num","M","A2"]
[null,null,"风机额定扬程","RatedFanHead","Pa","Num","M","A2"]
[null,null,"风机额定效率","RatedFanEff","%","Num","R","A2"]
[null,null,"风机额定转速","RatedFanRPM","rpm","Num","M","A2"]
[null,null,"叶轮直径","FanDiameter","mm","Num","R","A2"]
[null,null,"风机性能曲线","FanCharacterCurve ",null,"Attachment","R","F1"]
[null,null,"送风阀调节范围","SupplyValveRange","%","Numr","R","A2"]
[null,"其他","其他功能段","OtherFuncSection",null,"MEnum","R","D2","1. 空箱段 2. 均流段 3. 消声段 4. 中间段 99. 其他 （可多选）"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","R","L"]
[null,null,"B相电压","BPhaseU","V","Inst","R","L"]
[null,null,"C相电压","CPhaseU","V","Inst","R","L"]
[null,null,"A相电流","APhaseI","A","Inst","R","L"]
[null,null,"B相电流","BPhaseI","A","Inst","R","L"]
[null,null,"C相电流","CPhaseI","A","Inst","R","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"新风温度","FreshAirTemp","℃","Inst","M","L"]
[null,null,"新风相对湿度","FreshAirRH","%RH","Inst","M","L"]
[null,null,"新风颗粒物浓度","FreshAirPM","mg/m3","Inst","M","L"]
[null,null,"新风压力","FreshAirPress","Pa","Inst","R","L"]
[null,null,"新风量","FreshAirFlow","m3/h","Inst","R","L"]
[null,null,"新风口风速","FreshAirInV","m/s","Inst","R","L"]
[null,null,"新风阀开闭状态","FreshAirValveStatus",null,"Boolv","M","L","0. 关闭 1. 开启"]
[null,null,"新风阀开度","FreshAirValveOpening","%","Inst","M","L"]
[null,null,"新风滤网状态","FreshAirFilterStatus",null,"Enumv","R","L","1. 正常 2. 需更换 99. 其他"]
[null,null,"新风预热功率","FreshAirPreheatP","kW","Inst","R","L"]
[null,null,"新风热回收运行状态","FreshAirHeatRecoveryStatus",null,"Boolv","M","L","0. 停止 1. 运行"]
[null,null,"新风段出口温度","FreshAirOutTemp","℃","Inst","R","L"]
[null,null,"新风段出口相对湿度","FreshAirOutRH","%RH","Inst","R","L"]
[null,null,"新风段出口颗粒物浓度","FreshAirOutPM ","mg/m3","Inst","R","L"]
[null,null,"新风段出口压力","FreshAirOutPress","Pa","Inst","R","L"]
[null,null,"排风温度","ExhaustAirOutTemp","℃","Inst","R","L"]
[null,null,"排风相对湿度","ExhaustAirOutRH","%RH","Inst","R","L"]
[null,null,"排风压力","ExhaustAirOutPress","Pa","Inst","R","L"]
[null,null,"回风温度","ReturnAirTemp","℃","Inst","S","L"]
[null,null,"回风相对湿度","ReturnAirRH","%RH","Inst","M","L"]
[null,null,"回风颗粒物浓度","ReturnAirPM ","mg/m3","Inst","M","L"]
[null,null,"回风压力","ReturnAirPress","Pa","Inst","R","L"]
[null,null,"回风风量","ReturnAirFlow","m3/h","Inst","R","L",null,"一次回风系统"]
[null,null,"回风阀开度","ReturnAirValveOpening","%","Inst","M","L",null,"一次回风系统"]
[null,null,"一次回风风量","PrimaryReturnAirFlow","m3/h","Inst","R","L",null,"二次回风系统"]
[null,null,"一次回风阀开度","PrimarReturnAirValveOpening","%","Inst","R","L",null,"二次回风系统"]
[null,null,"混风段后温度","MixAirTemp","℃","Inst","R","L"]
[null,null,"混风段后相对湿度","MixAirRH","%RH","Inst","R","L"]
[null,null,"混风段后颗粒物浓度","MixAirPM","mg/m3","Inst","R","L"]
[null,null,"混风段后压力","MixAirPress","Pa","Inst","R","L"]
[null,null,"过滤段滤网工作状态","FilterStatus",null,"Inst","R","L","1. 正常 2. 需更换 99. 其他"]
[null,null,"过滤段后颗粒物浓度","FilterAirPM","mg/m3","Inst","R","L"]
[null,null,"过滤段后压力","FilterAirPress","Pa","Inst","R","L"]
[null,null,"冷水进口温度","ChillWaterInTemp","℃","Inst","M","L"]
[null,null,"冷水出口温度","ChillWaterOutTemp","℃","Inst","M","L"]
[null,null,"冷水流量","ChillWaterFlow","m3/h","Inst","R","L"]
[null,null,"冷水阀开度","ChillWaterValveOpening","%","Inst","S","L"]
[null,null,"制冷量","CoolP","kW","Inst","R","L"]
[null,null,"除湿量","DeD","g/h","Inst","R","L"]
[null,null,"热水进口温度","HotWaterInTemp","℃","Inst","M","L"]
[null,null,"热水出口温度","HotWater0utTemp","℃","Inst","M","L"]
[null,null,"热水流量","HotWaterFlow","m3/h","Inst","R","L"]
[null,null,"热水阀开度","HotWaterValveOpening","%","Inst","S","L"]
[null,null,"制热量","HeatP","kW","Inst","R","L"]
[null,null,"表冷段后温度","CoolCoilAirTemp","℃","Inst","R","L"]
[null,null,"表冷段后相对湿度","CoolCoilAirRH","%RH","Inst","R","L"]
[null,null,"表冷段后压力","CoolCoilAirPress","Pa","Inst","R","L"]
[null,null,"二次回风风量","SecondaryReturnAirFlow","m3/h","Inst","R","L",null,"二次回风系统"]
[null,null,"二次回风阀开度","SecondaryReturnAirValveOpening","%","Inst","M","L",null,"二次回风系统"]
[null,null,"二次混风段后温度","SecondaryMixAirTemp","℃","Inst","R","L",null,"二次回风系统"]
[null,null,"二次混风段后相对湿度","SecondaryMixAirRH","%RH","Inst","R","L",null,"二次回风系统"]
[null,null,"二次混风段后颗粒物浓度","SecondaryMixAirPM","mg/m3","Inst","R","L",null,"二次回风系统"]
[null,null,"二次混风段后压力","SecondaryMixAirPress","Pa","Inst","R","L",null,"二次回风系统"]
[null,null,"加湿量","D","g/h","Inst","R","L"]
[null,null,"加湿段后温度","DAirTemp","℃","Inst","R","L"]
[null,null,"加湿段后相对湿度","DAirRH","%RH","Inst","R","L"]
[null,null,"加湿段后压力","DAirPress","Pa","Inst","R","L"]
[null,null,"再热功率","ReheatP","kW","Inst","M","L"]
[null,null,"再热段后温度","ReheatAirTemp","℃","Inst","R","L"]
[null,null,"再热段后相对湿度","ReheatAirRH","%RH","Inst","R","L"]
[null,null,"再热段后压力","ReheatAirPress","Pa","Inst","R","L"]
[null,null,"送风量","SupplyAirFlow","m3/h","Inst","M","L"]
[null,null,"空调箱截面风速","CrossAirV","m/s","Inst","R","L"]
[null,null,"送风阀开度","SupplyAirValveOpening","%","Inst","M","L"]
[null,null,"风机频率","FanFreq","Hz","Inst","S","L"]
[null,null,"风机档位","FanGear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"风机转速","FanRPM","rpm","Inst","R","L"]
[null,null,"送风温度","SupplyAirTemp","℃","Inst","S","L"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","M","L"]
[null,null,"送风颗粒物浓度","SupplyAirPM","mg/m3","Inst","M","L"]
[null,null,"机外余压","ExcessPress","Pa","Inst","R","L"]
[null,"瞬时指标","新风段过滤效率","FreshAirFiltEff","%","Inst","R","M"]
[null,null,"新风热回收显热效率","FreshAirHeatRecoverySensibleHeatEff","%","Inst","R","M"]
[null,null,"新风热回收全热效率","FreshAirHeatRecoveryTotHeatEff","%","Inst","R","M"]
[null,null,"新风比","FreshAirRatio","%","Inst","R","M"]
[null,null,"机器露点","CoolCoilMachineDewdrop","%","Inst","R","M"]
[null,null,"表冷器换热效率","CoolCoilEff","%","Inst","R","M"]
[null,null,"过滤段过滤效率","FiltEff","%","Inst","R","M"]
[null,null,"空调箱阻力","AHUResistance","Pa","Inst","R","M"]
[null,null,"风机扬程","FanHead","Pa","Inst","R","M"]
[null,null,"风机效率","FanEff","%","Inst","R","M"]
[null,null,"风机输配系数","WTFfan",null,"Inst","R","M"]
[null,null,"末端负载率","PLR","%","Inst","R","M"]
[null,"累计指标","累计供冷量","AccCool","kWh","Acc","R","M"]
[null,null,"累计供热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计除湿量","AccDeD","kg","Acc","R","M"]
[null,null,"累计加湿量","AccD","kg","Acc","R","M"]
[null,null,"累计送风量","AccSupplyAir","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"风机频率设定","FanFreqSet","Hz","Boolp","S","L"]
[null,null,"风机档位设定","FanGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"送风温度设定","SupplyAirTempSet","℃","Nump","S","L"]
[null,null,"送风湿度设定","SupplyAirRHSet","%RH","Nump","S","L"]
[null,null,"回风温度设定","ReturnAirTempSet","℃","Nump","S","L"]
[null,null,"水阀开关设定","WaterValveSwitchSet",null,"Boolp","S","L","0. 关闭 1. 开启"]
[null,null,"水阀开度设定","WaterValveOpeningSet","%","Nump","S","L"]
[null,null,"新风阀开关设定","FreshAirValveSwitchSet",null,"Boolp","S","L","0. 关闭 1. 开启"]
[null,null,"新风阀开度设定","FreshAirValveOpeningSet","%","Nump","S","L"]
[null,null,"新风阀最大阀位设定","FreshAirValveMaxOpeningSet","%","Nump","S","L"]
[null,null,"回风阀开关设定","ReturnAirValveSwitchSet",null,"Boolp","S","L","0. 关闭 1. 开启"]
[null,null,"回风阀开度设定","ReturnAirValveOpeningSet","%","Nump","S","L"]
["报警消息",null,"初效过滤器报警","PrimFilterAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"中效过滤器报警","MedFilterAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"送风机故障报警","SupplyFanErrorAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"变频器故障报警","ConverterErrorAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"防冻报警","FrozenAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]

{"sheet":"ATFU新风机组","index":1,"n_rows":173,"n_cols":10,"rows_kept":173,"cut":false,"hidden":false,"merged":[[2,1,31,1],[157,0,167,1],[168,0,172,1],[1,0,1,1],[0,0,0,9],[75,0,156,0],[2,0,74,0],[138,1,147,1],[75,1,137,1],[148,1,156,1],[64,1,74,1],[32,1,35,1],[36,1,41,1],[42,1,58,1],[59,1,61,1],[62,1,63,1]]}
["新风机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"最小新风量","MinFreshAirFlow","m3/h","Num","R","A2"]
[null,null,"最大新风量","MaxFreshAirFlow","m3/h","Num","R","A2"]
[null,null,"新风阀调节范围","FreshAirValveRange","%","Numr","M","A2"]
[null,null,"设计机外余压","DesignExcessPress","Pa","Num","M","A2"]
[null,null,"夏季工况设计新风送风温度","SummerDesignFreshAirSupplyTemp","℃","Num","M","A2"]
[null,null,"夏季工况设计新风送风相对湿度","SummerDesignFreshAirSupplyRH","%RH","Num","M","A2"]
[null,null,"夏季工况设计新风量","SummerDesignFreshAirFlow","m3/h","Num","M","A2"]
[null,null,"冬季工况设计新风送风温度","WinterDesignFreshAirSupplyTemp","℃","Num","M","A2"]
[null,null,"冬季工况设计新风送风相对湿度","WinterDesignFreshAirSupplyRH","%RH","Num","M","A2"]
[null,null,"冬季工况设计新风量","WinterDesignFreshAirFlow","m3/h","Num","M","A2"]
[null,null,"新风口截面长度","FreshAirInletLength","m","Num","R","A2"]
[null,null,"新风口截面高度","FreshAirInletHeight","m","Num","R","A2"]
[null,null,"新风箱内部截面长度","CrossLength","m","Num","R","A2"]
[null,null,"新风箱内部截面高度","CrossHeight","m","Num","R","A2"]
[null,null,"漏风率","LeakageRatio ","%","Num","R","A2"]
[null,null,"功能段连接关系","SectionConnect",null,"Str","R","I"]
[null,null,"设计工况新风机组处理过程焓湿图","DesignIDGraph",null,"Attachment","R","F2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"过滤段","有无过滤段","isFilterSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"过滤段个数","FilterSectionNum","个","Num","R","A2"]
[null,null,"过滤方式","FilterType",null,"MEnum","R","D2","1. 初效过滤段 2. 中小过滤段 3. 亚高效过滤段 4. 高效过滤段 5. 活性炭过滤段 99. 其他 （可多选）"]
[null,null,"过滤效率","FilterRatedEff","%","Nums","R","A4"]
[null,"热回收段","有无热回收段","isHeatRecoverySection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"新风热回收类型","HeatRecoveryType",null,"Enum","M","D1","1. 无热回收 2. 板式 3. 转轮式 4. 热管式 5. 中间热媒式 6. 热泵式 99. 其他"]
[null,null,"夏季工况新风热回收显热效率","SummerDesignHeatRecoverySensibleHeatEff","%","Num","R","A2"]
[null,null,"夏季工况新风热回收全热效率","SummerDesignHeatRecoveryTotalHeatEff","%","Num","R","A2"]
[null,null,"冬季工况新风热回收显热效率","WinterDesignHeatRecoverySensibleHeatEff","%","Num","R","A2"]
[null,null,"冬季工况新风热回收全热效率","WinterDesignHeatRecoveryTotalHeatEff","%","Num","R","A2"]
[null,"表冷段","有无表冷段","isCoolCoilSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"夏季工况额定空气出口温度","SummerDesignCoolCoilAirOutTemp","℃","Num","R","A2"]
[null,null,"夏季工况额定空气出口相对湿度","SummerDesignCoolCoilAirOutRH","%RH","Num","R","A2"]
[null,null,"冬季工况额定空气出口温度","WinterDesignCoolCoilAirOutTemp","℃","Num","R","A2"]
[null,null,"冬季工况额定空气出口相对湿度","WinterDesignCoolCoilAirOutRH","%RH","Num","R","A2"]
[null,null,"空气侧换热面积","CoolCoilHeatTransArea","m2","Num","R","A2"]
[null,null,"设定机器露点","RatedCoolCoilMachineDewdrop","%","Num","R","A2"]
[null,null,"设计制冷量","DesignCoolP","kW","Num","M","A2"]
[null,null,"设计除湿量","DesignDeD","g/h","Num","M","A2"]
[null,null,"设计冷水进口温度","DesignChillWaterInTemp","℃","Num","R","A2"]
[null,null,"设计冷水出口温度","DesignChillWaterOutTemp","℃","Num","R","A2"]
[null,null,"设计冷水流量","DesignChillWaterFlow","m3/h","Num","R","A2"]
[null,null,"有无热水加热功能","isHotWaterFunc",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"设计制热量","DesignHeatP","kW","Num","M","A2"]
[null,null,"设计热水进口温度","DesignHotWaterInTemp","℃","Num","R","A2"]
[null,null,"设计热水出口温度","DesignHotWaterOutTemp","℃","Num","R","A2"]
[null,null,"设计热水流量","DesignHotWaterFlow","m3/h","Num","R","A2"]
[null,"加湿段","有无加湿段","isDSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"加湿方式","DType",null,"Enum","R","D1","1. 湿膜式 2. 超声波式 3. 电热式 4. 高压喷雾式 5. 干蒸汽式 6. 离心式 99. 其他"]
[null,null,"最大加湿量","MaxD","g/h","Num","R","A2"]
[null,"再热段","有无再热段","isReheatSection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"最大加热功率","MaxReheatP","kW","Num","R","A2"]
[null,"送风段","有无送风段","isSupplySection",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"风机类型","FanType",null,"Enum","M","D1","1. 离心风机 2. 轴流风机 3. 贯流风机 99. 其他"]
[null,null,"风机有无变频功能","isFanVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"风机有无档位选择","isFanGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"风机额定频率","RatedFanFreq","Hz","Num","M","A2"]
[null,null,"风机额定风量","RatedFanFlow","m3/h","Num","M","A2"]
[null,null,"风机额定扬程","RatedFanHead","Pa","Num","M","A2"]
[null,null,"风机额定效率","RatedFanEff","%","Num","R","A2"]
[null,null,"风机额定转速","RatedFanRPM","rpm","Num","M","A2"]
[null,null,"叶轮直径","FanDiameter","m","Num","R","A2"]
[null,null,"风机性能曲线","FanCharacterCurve ",null,"Attachment","R","F1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","R","L"]
[null,null,"B相电压","BPhaseU","V","Inst","R","L"]
[null,null,"C相电压","CPhaseU","V","Inst","R","L"]
[null,null,"A相电流","APhaseI","A","Inst","R","L"]
[null,null,"B相电流","BPhaseI","A","Inst","R","L"]
[null,null,"C相电流","CPhaseI","A","Inst","R","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"新风温度","FreshAirTemp","℃","Inst","M","L"]
[null,null,"新风相对湿度","FreshAirRH","%RH","Inst","M","L"]
[null,null,"新风颗粒度浓度","FreshAirPM","mg/m3","Inst","M","L"]
[null,null,"新风压力","FreshAirPress","Pa","Inst","R","L"]
[null,null,"新风量","FreshAirFlow","m3/h","Inst","M","L"]
[null,null,"新风口风速","FreshAirInV","m/s","Inst","R","L"]
[null,null,"新风阀开闭状态","FreshAirValveStatus",null,"Boolv","M","L","0. 关闭 1. 开启"]
[null,null,"新风阀开度","FreshAirValveOpening","%","Inst","M","L"]
[null,null,"过滤段滤网工作状态","FilterStatus",null,"Enumv","R","L","1. 正常 2. 需更换 99. 其他"]
[null,null,"过滤段后颗粒度浓度","FiltAirPM","mg/m3","Inst","R","L"]
[null,null,"过滤段后压力","FiltAirPress","Pa","Inst","R","L"]
[null,null,"热回收装置运行状态","HeatRecoveryStatus",null,"Boolv","M","L","0. 停止 1. 运行"]
[null,null,"热回收段出口温度","HeatRecoveryAirTemp","℃","Inst","R","L"]
[null,null,"热回收段出口相对湿度","HeatRecoveryAirRH","%RH","Inst","R","L"]
[null,null,"热回收段出口压力","HeatRecoveryAirPress","Pa","Inst","R","L"]
[null,null,"热回收后排风温度","ExhaustAirOutTemp","℃","Inst","R","L"]
[null,null,"热回收后排风相对湿度","ExhaustAirOutRH","%RH","Inst","R","L"]
[null,null,"热回收后排风压力","ExhaustAirOutPress","Pa","Inst","R","L"]
[null,null,"冷水进口温度","ChillWaterInTemp","℃","Inst","M","L"]
[null,null,"冷水出口温度","ChillWaterOutTemp","℃","Inst","M","L"]
[null,null,"冷水流量","ChillWaterFlow","m3/h","Inst","R","L"]
[null,null,"冷水阀开度","ChillWaterValveOpening","%","Inst","S","L"]
[null,null,"制冷量","CoolP","kW","Inst","R","L"]
[null,null,"除湿量","DeD","g/h","Inst","R","L"]
[null,null,"热水进口温度","HotWaterInTemp","℃","Inst","M","L"]
[null,null,"热水出口温度","HotWater0utTemp","℃","Inst","M","L"]
[null,null,"热水流量","HotWaterFlow","m3/h","Inst","R","L"]
[null,null,"热水阀开度","HotWaterValveOpening","%","Inst","S","L"]
[null,null,"制热量","HeatP","kW","Inst","R","L"]
[null,null,"表冷段后温度","CoolCoilAirTemp","℃","Inst","R","L"]
[null,null,"表冷段后相对湿度","CoolCoilAirRH","%RH","Inst","R","L"]
[null,null,"表冷段后压力","CoolCoilAirPress","Pa","Inst","R","L"]
[null,null,"加湿器状态","DStatus",null,"Boolv","R","L","0. 关闭 1. 开启"]
[null,null,"加湿量","D","g/h","Inst","R","L"]
[null,null,"加湿段后温度","DAirTemp","℃","Inst","R","L"]
[null,null,"加湿段后相对湿度","DAirRH","%RH","Inst","R","L"]
[null,null,"加湿段后压力","DAirPress","Pa","Inst","R","L"]
[null,null,"再热功率","ReheatP","kW","Inst","M","L"]
[null,null,"再热段后温度","ReheatAirTemp","℃","Inst","R","L"]
[null,null,"再热段后相对湿度","ReheatAirRH","%RH","Inst","R","L"]
[null,null,"再热段后压力","ReheatAirPress","Pa","Inst","R","L"]
[null,null,"新风箱截面风速","CrossAirV","m/s","Inst","R","L"]
[null,null,"风机频率","FanFreq","Hz","Inst","S","L"]
[null,null,"风机档位","FanGear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"风机转速","FanRPM","rpm","Inst","R","L"]
[null,null,"送风温度","SupplyAirTemp","℃","Inst","S","L"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","M","L"]
[null,null,"送风颗粒物浓度","SupplyAirPM","mg/m3","Inst","M","L"]
[null,null,"机外余压","ExcessPress","Pa","Inst","R","L"]
[null,"瞬时指标","过滤段过滤效率","FiltEff","%","Inst","R","M"]
[null,null,"新风热回收显热效率","HeatRecoverySensibleHeatEff","%","Inst","R","M"]
[null,null,"新风热回收全热效率","HeatRecoveryTotHeatEff","%","Inst","R","M"]
[null,null,"机器露点","CoolCoilMachineDewdrop","%","Inst","R","M"]
[null,null,"表冷器换热效率","CoolCoilEff","%","Inst","R","M"]
[null,null,"空调箱阻力","FAUResistance","Pa","Inst","R","M"]
[null,null,"风机扬程","FanHead","Pa","Inst","R","M"]
[null,null,"风机效率","FanEff","%","Inst","R","M"]
[null,null,"风机输配系数","FanWTF",null,"Inst","R","M"]
[null,null,"末端负载率","PLR","%","Inst","R","M"]
[null,"累计指标","累计供冷量","AccCool","kWh","Acc","R","M"]
[null,null,"累计供热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计除湿量","AccDeD","kg","Acc","R","M"]
[null,null,"累计加湿量","AccD","kg","Acc","R","M"]
[null,null,"累计新风量","AccFreshAir","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"风机频率设定","FanFreqSet","Hz","Boolp","S","L"]
[null,null,"风机档位设定","FanGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"送风温度设定","SupplyAirTempSet","℃","Nump","S","L"]
[null,null,"送风湿度设定","SupplyAirRHSet","%RH","Nump","S","L"]
[null,null,"室内温度设定","IndoorAirTempSet","℃","Nump","S","L"]
[null,null,"室内CO2浓度设定","IndoorAirCO2Set","ppm","Nump","S","L"]
[null,null,"水阀开关设定","WaterValveSwitchSet",null,"Boolp","S","L","0. 关闭 1. 开启"]
[null,null,"水阀开度设定","WaterValveOpeningSet","%","Nump","S","L"]
[null,null,"新风阀开关设定","FreshAirValveSwitchSet",null,"Boolp","S","L","0. 关闭 1. 开启"]
[null,null,"新风阀开度设定","FreshAirValveOpeningSet","%","Nump","S","L"]
["报警消息",null,"初效过滤器报警","PrimFilterAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"中效过滤器报警","MedFilterAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"送风机故障报警","SupplyFanErrorAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"变频器故障报警","ConverterErrorAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"防冻报警","FrozenAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]

{"sheet":"ATFC风机盘管","index":2,"n_rows":116,"n_cols":10,"rows_kept":116,"cut":false,"hidden":false,"merged":[[109,0,113,1],[114,0,115,1],[15,1,23,1],[0,0,0,9],[1,0,1,1],[2,0,56,0],[24,1,56,1],[63,1,70,1],[57,1,62,1],[71,1,94,1],[95,1,108,1],[57,0,108,0],[2,1,14,1]]}
["风机盘管"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","盘管类型","CoilType",null,"Enum","S","D1","1. 双管制 2. 四管制 99. 其他"]
[null,null,"排管数量","CoilRowType",null,"Enum","R","D1","1. 两排管 2. 三排管 99. 其他"]
[null,null,"安装类型","InstallType",null,"Enum","R","D1","1. 卧式暗装 2. 卧式明装 3. 立式暗装 4. 立式明装 5. 卡式 99. 其他"]
[null,null,"冷水温度类型","ChillWaterType",null,"Enum","R","D1","1. 湿式盘管 2. 干式盘管 99. 其他"]
[null,null,"是否有供热功能","isHeatFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"风口宽","OutletWidth","m","Num","R","A2"]
[null,null,"风口高","OutletHeight","m","Num","R","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"风机","风机有无变频功能","isFanVFD",null,"Bool","S","E1"]
[null,null,"风机有无档位选项","isFanGear",null,"Bool","S","E1"]
[null,null,"风机额定电压","RatedFanU","V","Num","M","A2"]
[null,null,"风机额定电流","RatedFanI","A","Num","M","A2"]
[null,null,"风机额定功率","RatedFanP","kW","Num","M","A2"]
[null,null,"风机额定频率","RatedFanFreq","Hz","Num","M","A2"]
[null,null,"风机档位数","FanGearNum","档","Num","M","A2"]
[null,null,"风机额定风量","RatedFanFlow","m3/h","Num","M","A2"]
[null,null,"风机额定扬程","RatedFanHead","Pa","Num","R","A2"]
[null,"盘管","夏季工况盘管设计进水温度","SummerDesignWaterInTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"夏季工况盘管设计出水温度","SummerDesignWaterOutTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"夏季工况盘管设计流量","SummerDesignWaterFlow","m3/h","Num","R","A2",null,"两管制"]
[null,null,"夏季工况盘管设计冷水进水温度","SummerDesignChillWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计冷水出水温度","SummerDesignChillWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计冷水流量","SummerDesignChillWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计热水进水温度","SummerDesignHotWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计热水出水温度","SummerDesignHotWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计热水流量","SummerDesignHotWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"夏季工况设计回风温度","SummerDesignReturnAirTemp","℃","Num","R","A2"]
[null,null,"夏季工况设计回风相对湿度","SummerDesignReturnAirRH","%RH","Num","R","A2"]
[null,null,"夏季工况设计送风温度","SummerDesignSupplyAirTemp","℃","Num","R","A2"]
[null,null,"夏季工况设计送风相对湿度","SummerDesignSupplyAirRH","%RH","Num","R","A2"]
[null,null,"夏季工况设计循环风量","SummerDesignSupplyAirFlow","m3/h","Num","R","A2"]
[null,null,"冬季工况盘管设计进水温度","WinterDesignWaterInTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"冬季工况盘管设计出水温度","WinterDesignWaterOutTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"冬季工况盘管设计流量","WinterDesignWaterFlow","m3/h","Num","R","A2",null,"两管制"]
[null,null,"冬季工况盘管设计冷水进水温度","WinterDesignChillWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计冷水出水温度","WinterDesignChillWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计冷水流量","WinterDesignChillWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计热水进水温度","WinterDesignHotWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计热水出水温度","WinterDesignHotWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计热水流量","WinterDesignHotWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"冬季工况设计回风温度","WinterDesignReturnAirTemp","℃","Num","R","A2"]
[null,null,"冬季工况设计回风相对湿度","WinterDesignReturnAirRH","%RH","Num","R","A2"]
[null,null,"冬季工况设计送风温度","WinterDesignSupplyAirTemp","℃","Num","R","A2"]
[null,null,"冬季工况设计送风相对湿度","WinterDesignSupplyAirRH","%RH","Num","R","A2"]
[null,null,"冬季工况设计循环风量","WinterDesignSupplyAirFlow","m3/h","Num","R","A2"]
[null,null,"盘管水阀调节范围","WaterValveRange","%","Num","R","A6"]
[null,null,"盘管压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"设计供冷量","DesignCoolP","kW","Num","M","A2"]
[null,null,"设计除湿量","DesignDeD","g/h","Num","R","A2"]
[null,null,"设计供热量","DesignHeatP","kW","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"FCU工作模式","WorkMode",null,"Enumv","S","L","1. 供冷 2. 供热 99. 其他"]
[null,"风机","平均电压","U","V","Inst","R","L"]
[null,null,"平均电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"风机工作频率","FanFreq","Hz","Inst","R","L"]
[null,null,"风机档位","FanGear",null,"Enumv","S","L","0. 关 1. 低 2. 中 3. 高 99. 其他"]
[null,null,"循环风量","SupplyAirFlow","m3/h","Inst","R","L"]
[null,null,"出口风速","SupplyAirV","m/s","Inst","R","L"]
[null,null,"送风压力","SupplyAirPress","Pa","Inst","R","L"]
[null,"盘管","盘管进水温度","WaterInTemp","℃","Inst","M","L",null,"两管制"]
[null,null,"盘管出水温度","WaterOutTemp","℃","Inst","M","L",null,"两管制"]
[null,null,"盘管循环水量","WaterFlow","m3/h","Inst","R","L",null,"两管制"]
[null,null,"盘管水阀开关状态","WaterValveSwitchStatus",null,"Boolv","M",null,"0. 关闭 1. 开启","两管制"]
[null,null,"盘管水阀开度","WaterValveOpening","%","Inst","M","L",null,"两管制"]
[null,null,"盘管冷水进水温度","ChillWaterInTemp","℃","Inst","M","L",null,"四管制"]
[null,null,"盘管冷水出水温度","ChillWaterOutTemp","℃","Inst","M","L",null,"四管制"]
[null,null,"盘管冷水流量","ChillWaterFlow","m3/h","Inst","R","L",null,"四管制"]
[null,null,"盘管热水进水温度","HotWaterInTemp","℃","Inst","M","L",null,"四管制"]
[null,null,"盘管热水出水温度","HotWaterOutTemp","℃","Inst","M","L",null,"四管制"]
[null,null,"盘管热水流量","HotWaterFlow","m3/h","Inst","R","L",null,"四管制"]
[null,null,"盘管冷水阀开关状态","ChillWaterValveSwitchStatus",null,"Boolv","M",null,"0. 关闭 1. 开启","四管制"]
[null,null,"盘管冷水阀开度","ChillWaterValveOpening","%","Inst","M","L",null,"四管制"]
[null,null,"盘管热水阀开关状态","HotWaterValveSwitchStatus",null,"Boolv","M",null,"0. 关闭 1. 开启","四管制"]
[null,null,"盘管热水阀开度","HotWaterValveOpening","%","Inst","M","L",null,"四管制"]
[null,null,"盘管进水压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"盘管出水压力","WaterOutPress","MPa","Inst","R","L"]
[null,null,"回风温度","ReturnAirTemp","℃","Inst","M","L"]
[null,null,"回风相对湿度","ReturnAirRH","%RH","Inst","R","L"]
[null,null,"送风温度","SupplyTemp","℃","Inst","M","L"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","R","L"]
[null,null,"供冷量","CoolP","kW","Inst","R","M"]
[null,null,"除湿量","DeD","g/h","Inst","R","M"]
[null,null,"供热量","HeatP","kW","Inst","R","M"]
[null,"累计指标","累计供冷量","AccCool","kWh","Acc","R","M"]
[null,null,"累计除湿量","AccDeD","kg","Acc","R","M"]
[null,null,"累计供热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计水流量","AccWater","m3","Acc","R","M",null,"两管制"]
[null,null,"累计冷水流量","AccChillWater","m3","Acc","R","M",null,"四管制"]
[null,null,"累计热水流量","AccHotWater","m3","Acc","R","M",null,"四管制"]
[null,null,"累计送风量","AccSupplyAir","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"低档位累计运行时间","AccLowGearRunTime","h","Acc","M","M"]
[null,null,"中档位累计运行时间","AccMiddleGearRunTime","h","Acc","M","M"]
[null,null,"高档位累计运行时间","AccHighGearRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 关闭 1. 开启"]
[null,null,"风机频率设定","FanFreqSet","Hz","Nump","S","L"]
[null,null,"风机档位设定","FanGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"盘管水阀开关状态设定","WaterValveSwitchSet",null,"Boolv","M",null,"0. 关闭 1. 开启","两管制"]
[null,null,"室内温度设定","IndoorAirTempSet","℃","Nump","S","L"]
["报警消息",null,"过滤网压差报警","FilterDetaPressAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"风机故障报警","FanErrorAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]

{"sheet":"ATSA分体空调","index":3,"n_rows":57,"n_cols":10,"rows_kept":57,"cut":false,"hidden":false,"merged":[[55,0,55,1],[56,0,56,1],[0,0,0,9],[1,0,1,1],[26,0,54,0],[26,1,45,1],[47,1,54,1],[2,0,25,1]]}
["分体空调"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"滤袋个数","FilterNum","个","Num","R","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","R","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"功能模式类型","FuncType",null,"MEnum","S","D2","1. 制冷 2. 制热 2. 通风 4. 除湿 99. 其他 （可多选）"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"制冷适用面积","RatedCoolArea","m2","Num","R","A2"]
[null,null,"制热适用面积","RatedHeatArea","m2","Num","R","A2"]
[null,null,"额定制冷功率","RatedCoolP","kW","Num","S","A2"]
[null,null,"额定制热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定除湿量","RatedDeD","g/h","Num","R","A2"]
[null,null,"最大电加热功率","MaxElecHeatP","kW","Num","R","A2"]
[null,null,"额定风量","RatedAirFlow","m3/h","Num","M","A2"]
[null,null,"能效比","RatedCOP",null,"Num","M","A1"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","RunMode",null,"Enumv","M","L","1. 制冷 2. 制热 3. 通风 4. 除湿 99. 其他"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"工作频率","Freq","Hz","Inst","R","L"]
[null,null,"回风温度","ReturnAirTemp","℃","Inst","M","L"]
[null,null,"回风相对湿度","ReturnAirRH","%RH","Inst","R","L"]
[null,null,"送风温度","SupplyAirTemp","℃","Inst","M","L"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","R","L"]
[null,null,"循环风量","SupplyAirFlow","m3/h","Inst","R","L"]
[null,null,"出口风速","SupplyAirV","m/s","Inst","R","L"]
[null,null,"制冷功率","CoolP","kW","Inst","R","L"]
[null,null,"制热功率","HeatP","kW","Inst","R","L"]
[null,null,"除湿量","DeD","g/h","Inst","R","L"]
[null,null,"电辅热功率","ElecHeatP","kW","Inst","R","L"]
[null,"瞬时指标","COP","COP",null,"Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","R","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计除湿量","AccDeD","kg","Acc","R","M"]
[null,null,"累计送风量","AccSupplyAir","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ATVR变频多联机","index":4,"n_rows":61,"n_cols":10,"rows_kept":61,"cut":false,"hidden":false,"merged":[[59,0,59,1],[60,0,60,1],[0,0,0,9],[1,0,1,1],[27,1,48,1],[27,0,58,0],[2,0,26,1],[50,1,58,1]]}
["变频多联机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"室外机额定电流","RatedOutUnitI","A","Num","M","A2"]
[null,null,"室外机额定功率","RatedOutUnitP","kW","Num","S","A2"]
[null,null,"单台室内机额定电流","RatedSingleInUnitI","A","Num","M","A2"]
[null,null,"单台室内机额定功率","RatedSingleInUnitP","kW","Num","S","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"功能模式类型","FuncType",null,"MEnum","S","D2","1. 制冷 2. 制热 2. 通风 4. 除湿 99. 其他 （可多选）"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"室内机数量","InUnitNum","台","Num","S","A2"]
[null,null,"单台室内机滤袋个数","SingleInUnitFilterNum","个","Num","R","A2"]
[null,null,"单台室内机额定制冷功率","RatedSingleInUnitCoolP","kW","Num","S","A2"]
[null,null,"单台室内机额定制热功率","RatedSingleInUnitHeatP","kW","Num","S","A2"]
[null,null,"单台室内机额定除湿量","RatedSingleInUnitDeD","g/h","Num","M","A2"]
[null,null,"单台室内机最大电加热功率","MaxSingleInUnitElecHeatP","kW","Num","M","A2"]
[null,null,"单台室内机额定风量","RatedSingleInUnitAirFlow","kW","Num","M","A2"]
[null,null,"能效比","RatedCOP",null,"Num","M","A1"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","WorkMode",null,"Enumv","S","L","1. 制冷 2. 制热 3. 通风 4. 除湿 99. 其他"]
[null,null,"工作电压","U","V","Inst","S","L"]
[null,null,"室外机电流","OutUnitI","A","Inst","M","L"]
[null,null,"室外机耗电功率","OutUnitElecConsumP","kW","Inst","S","L"]
[null,null,"工作频率","Freq","Hz","Inst","S","L"]
[null,null,"室内机电流","InUnitI","A","Inst","M","L",null,"室内机序列"]
[null,null,"室内机耗电功率","InUnitElecConsumP","kW","Inst","S","L",null,"室内机序列"]
[null,null,"回风温度","ReturnAirTemp","℃","Inst","S","L",null,"室内机序列"]
[null,null,"回风相对湿度","ReturnAirRH","%RH","Inst","M","L",null,"室内机序列"]
[null,null,"送风温度","SupplyAirTemp","℃","Inst","S","L",null,"室内机序列"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","M","L",null,"室内机序列"]
[null,null,"循环风量","SupplyAirFlow","m3/h","Inst","M","L",null,"室内机序列"]
[null,null,"出口风速","SupplyAirV","m/s","Inst","M","L",null,"室内机序列"]
[null,null,"制冷功率","CoolP","kW","Inst","S","L",null,"室内机序列"]
[null,null,"制热功率","HeatP","kW","Inst","S","L",null,"室内机序列"]
[null,null,"除湿量","DeD","g/h","Inst","M","L",null,"室内机序列"]
[null,null,"电辅热功率","ElecHeatP","kW","Inst","M","L",null,"室内机序列"]
[null,"瞬时指标","COP","COP",null,"Inst","M","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计除湿量","AccDeD","kg","Acc","M","M"]
[null,null,"累计送风量","AccSupplyAir","m3","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ATVA变风量箱","index":5,"n_rows":28,"n_cols":10,"rows_kept":28,"cut":false,"hidden":false,"merged":[[26,0,26,1],[27,0,27,1],[11,0,25,0],[0,0,0,9],[1,0,1,1],[11,1,20,1],[21,1,25,1],[2,0,10,1]]}
["变风量箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","R","A2"]
[null,null,"额定电压","RatedU","V","Num","M","A2"]
[null,null,"额定电流","RatedI","A","Num","R","A2"]
[null,null,"额定功率","RatedP","kW","Num","M","A2"]
[null,null,"最小风量","MinAirFlow","m3/h","Num","M","A2"]
[null,null,"最大风量","MaxAirFlow","m3/h","Num","M","A2"]
[null,null,"额定风量","RatedAirFlow","m3/h","Num","M","A2"]
[null,null,"额定出口静压","RatedStaticPress","Pa","Num","M","A2"]
[null,null,"最小静压降","MinStaticPressDrop","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"瞬时风量","SupplyAirFlow","m3/h","Inst","M","L"]
[null,null,"送风温度","SupplyAirTemp","℃","Inst","M","L"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","R","L"]
[null,null,"送风压力","SupplyAirPress","Pa","Inst","R","L"]
[null,"累计指标","累计送风量","AccSupplyAir","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ATFA地板空调器","index":6,"n_rows":83,"n_cols":10,"rows_kept":83,"cut":false,"hidden":false,"merged":[[81,0,81,1],[82,0,82,1],[0,0,0,9],[57,0,80,0],[1,0,1,1],[57,1,73,1],[74,1,80,1],[2,0,56,0],[15,1,23,1],[24,1,56,1],[2,1,14,1]]}
["地板空调器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","盘管类型","CoilType",null,"Enum","S","D1","1. 双管制 2. 四管制 99. 其他"]
[null,null,"排管数量","CoilRowType",null,"Enum","R","D1","1. 两排管 2. 三排管 99. 其他"]
[null,null,"安装类型","InstallType",null,"Enum","R","D1","1. 卧式暗装 2. 卧式明装 3. 立式暗装 4. 立式明装 5. 卡式 99. 其他"]
[null,null,"冷水温度类型","ChillWaterType",null,"Enum","R","D1","1. 湿式盘管 2. 干式盘管 99. 其他"]
[null,null,"是否有供热功能","isHeatFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"风口宽","OutletWidth","m","Num","R","A2"]
[null,null,"风口高","OutletHeight","m","Num","R","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"风机","风机有无变频功能","isFanVFD",null,"Bool","S","E1"]
[null,null,"风机有无档位选项","isFanGear",null,"Bool","S","E1"]
[null,null,"风机额定电压","RatedFanU","V","Num","M","A2"]
[null,null,"风机额定电流","RatedFanI","A","Num","M","A2"]
[null,null,"风机额定功率","RatedFanP","kW","Num","M","A2"]
[null,null,"风机额定频率","RatedFanFreq","Hz","Num","M","A2"]
[null,null,"风机档位数","FanGearNum","档","Num","M","A2"]
[null,null,"风机额定风量","RatedFanFlow","m3/h","Num","M","A2"]
[null,null,"风机额定扬程","RatedFanHead","Pa","Num","R","A2"]
[null,"盘管","夏季工况盘管设计进水温度","SummerDesignWaterInTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"夏季工况盘管设计出水温度","SummerDesignWaterOutTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"夏季工况盘管设计流量","SummerDesignWaterFlow","m3/h","Num","R","A2",null,"两管制"]
[null,null,"夏季工况盘管设计冷水进水温度","SummerDesignChillWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计冷水出水温度","SummerDesignChillWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计冷水流量","SummerDesignChillWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计热水进水温度","SummerDesignHotWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计热水出水温度","SummerDesignHotWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"夏季工况盘管设计热水流量","SummerDesignHotWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"夏季工况设计回风温度","SummerDesignReturnAirTemp","℃","Num","R","A2"]
[null,null,"夏季工况设计回风相对湿度","SummerDesignReturnAirRH","%RH","Num","R","A2"]
[null,null,"夏季工况设计送风温度","SummerDesignSupplyAirTemp","℃","Num","R","A2"]
[null,null,"夏季工况设计送风相对湿度","SummerDesignSupplyAirRH","%RH","Num","R","A2"]
[null,null,"夏季工况设计循环风量","SummerDesignSupplyAirFlow","m3/h","Num","R","A2"]
[null,null,"冬季工况盘管设计进水温度","WinterDesignWaterInTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"冬季工况盘管设计出水温度","WinterDesignWaterOutTemp","℃","Num","R","A2",null,"两管制"]
[null,null,"冬季工况盘管设计流量","WinterDesignWaterFlow","m3/h","Num","R","A2",null,"两管制"]
[null,null,"冬季工况盘管设计冷水进水温度","WinterDesignChillWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计冷水出水温度","WinterDesignChillWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计冷水流量","WinterDesignChillWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计热水进水温度","WinterDesignHotWaterInTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计热水出水温度","WinterDesignHotWaterOutTemp","℃","Num","R","A2",null,"四管制"]
[null,null,"冬季工况盘管设计热水流量","WinterDesignHotWaterFlow","m3/h","Num","R","A2",null,"四管制"]
[null,null,"冬季工况设计回风温度","WinterDesignReturnAirTemp","℃","Num","R","A2"]
[null,null,"冬季工况设计回风相对湿度","WinterDesignReturnAirRH","%RH","Num","R","A2"]
[null,null,"冬季工况设计送风温度","WinterDesignSupplyAirTemp","℃","Num","R","A2"]
[null,null,"冬季工况设计送风相对湿度","WinterDesignSupplyAirRH","%RH","Num","R","A2"]
[null,null,"冬季工况设计循环风量","WinterDesignSupplyAirFlow","m3/h","Num","R","A2"]
[null,null,"盘管水阀调节范围","WaterValveRange","%","Num","R","A6"]
[null,null,"盘管压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"设计供冷量","DesignCoolP","kW","Num","M","A2"]
[null,null,"设计除湿量","DesignDeD","g/h","Num","R","A2"]
[null,null,"设计供热量","DesignHeatP","kW","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"平均电压","U","V","Inst","R","L"]
[null,null,"平均电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"回风温度","ReturnAirTemp","℃","Inst","R","L"]
[null,null,"回风相对湿度","ReturnAirRH","%RH","Inst","R","L"]
[null,null,"送风温度","SupplyAirTemp","℃","Inst","R","L"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","R","L"]
[null,null,"送风压力","SupplyAirPress","Pa","Inst","R","L"]
[null,null,"送风量","SupplyAirFlow","m3/h","Inst","R","L"]
[null,null,"出风速度","SupplyAirV","m/s","Inst","R","L"]
[null,null,"制冷量","CoolP","kW","Inst","R","L"]
[null,null,"制热量","HeatP","kW","Inst","R","L"]
[null,"累计指标","累计供冷量","AccCool","kWh","Acc","R","M"]
[null,null,"累计供热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计送风量","AccSupplyAir","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ATIO空调风口","index":7,"n_rows":13,"n_cols":10,"rows_kept":13,"cut":false,"hidden":false,"merged":[[12,0,12,1],[0,0,0,9],[1,0,1,1],[7,0,10,1],[11,0,11,1],[2,0,6,1]]}
["风口"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"材质","MaterialType",null,"Enum","R","D1","1. 铁板 2. 镀锌板 3. 铝合金板 4. 不锈钢板 99. 其他"]
[null,null,"类型","StructureType",null,"Enum","M","D1","1. 单层百叶风口 2. 双层百叶风口 3. 固定条形风口 4. 自垂百叶式风口 5. 散流器 6. 球形可调风口 7. 旋流风口 99. 其他"]
[null,null,"形状","ShapeType",null,"Enum","M","D1","1. 正方形 2. 矩形 3. 圆形 99. 其他"]
[null,null,"壁厚","Thick","mm","Num","R","A2"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"进口风压","AirInPress","Pa","Inst","R","L"]
[null,null,"出口风压","AirOutPress","Pa","Inst","R","L"]
[null,null,"瞬时风量","AirFlow","m3/h","Inst","R","L"]
[null,null,"瞬时风温","AirTemp","℃","Inst","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"ATRD散热器","index":8,"n_rows":48,"n_cols":10,"rows_kept":48,"cut":false,"hidden":false,"merged":[[46,0,46,1],[47,0,47,1],[42,1,45,1],[2,0,26,1],[0,0,0,9],[1,0,1,1],[27,0,45,0],[27,1,40,1]]}
["散热器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"材料类型","MaterialType",null,"Enum","R","D1","1. 铸铁 2. 钢 3. 铝合金 4. 铜管 5. 复合型 99. 其他"]
[null,null,"形状类型","ShapeType",null,"Enum","R","D1","1. 柱型 2. 长翼型 3. 圆翼型 4. 定向对流型 5. 钢串片型 6. 板型 7. 扁管型 8. 环形 9. 翅片型 10. 装饰型 99. 其他"]
[null,null,"进出口是否在同侧","isInOutSameSide",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"进出口中心距","InOutCenterDistance","mm","Num","R","A2"]
[null,null,"高度","Height","mm","Num","R","A2"]
[null,null,"宽度","Width","mm","Num","R","A2"]
[null,null,"长度","Length","mm","Num","R","A2"]
[null,null,"厚度","Thickness","mm","Num","R","A2"]
[null,null,"有效散热面积","EffectiveRadiantArea","m2","Num","R","A2"]
[null,null,"传热系数","HeatTransCoeff","W/(m2K)","Num","R","A2"]
[null,null,"额定散热量","RatedHeatRelease","kW","Num","M","A2"]
[null,null,"接口直径","InterfaceD","mm","Num","R","A2"]
[null,null,"额定进水温度","RatedInWaterTemp","℃","Num","M","A2",null,"热水"]
[null,null,"额定出水温度","RatedOutWaterTemp","℃","Num","R","A2",null,"热水"]
[null,null,"额定进水压力","RatedInWaterPress","MPa","Num","M","A2",null,"热水"]
[null,null,"额定出水压力","RatedOutWaterPress","MPa","Num","R","A2",null,"热水"]
[null,null,"额定热水流量","RatedWaterFlow","m3/h","Num","R","A2",null,"热水"]
[null,null,"额定进口蒸汽压力","RatedInVaporPress","MPa","Num","M","A2",null,"蒸汽"]
[null,null,"额定出口蒸汽压力","RatedOutVaporPress","MPa","Num","R","A2",null,"蒸汽"]
[null,null,"额定蒸汽流量","RatedVaporFlow","t/h","Num","R","A2",null,"蒸汽"]
[null,null,"热水试验压力","HotWaterTestPress","MPa","Num","M","A2"]
[null,null,"蒸汽试验压力","VaporTestPress","MPa","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"进口水温","InWaterTemp","℃","Inst","M","L",null,"热水"]
[null,null,"出口水温","OutWaterTemp","℃","Inst","M","L",null,"热水"]
[null,null,"进口水压","InWaterPress","MPa","Inst","R","L"]
[null,null,"出口水压","OutWaterPress","MPa","Inst","R","L"]
[null,null,"热水流量","WaterFlow","m3/h","Inst","R","L",null,"热水"]
[null,null,"进口蒸汽压力","InVaporPress","MPa","Inst","M","L",null,"蒸汽"]
[null,null,"出口蒸汽压力","OutVaporPress","MPa","Inst","M","L",null,"蒸汽"]
[null,null,"蒸汽流量","VaporFlow","t/h","Inst","R","L",null,"蒸汽"]
[null,null,"散热功率","HeatReleaseP","kW","Inst","R","L"]
[null,"瞬时指标","散热效率","HeatReleaseEff","%","Inst","R","M"]
[null,"累计指标","累计散热量","AccHeatRelease","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ATFH地板采暖设备","index":9,"n_rows":51,"n_cols":10,"rows_kept":51,"cut":false,"hidden":false,"merged":[[49,0,49,1],[50,0,50,1],[44,1,48,1],[0,0,0,9],[1,0,1,1],[25,0,48,0],[2,0,24,0],[3,1,7,1],[13,1,19,1],[8,1,12,1],[20,1,24,1],[25,1,42,1]]}
["地板采暖设备"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","设备类型","HeatType",null,"Enum","S","D1","1. 水地暖设备 2. 碳晶地暖设备 3. 发热电缆设备 4. 发热地膜设备 99. 其他"]
[null,"水地暖设备","水地暖额定供水温度","WaterHeatRatedWaterInTemp","℃","Num","M","A2"]
[null,null,"水地暖额定回水温度","WaterHeatRatedWaterOutTemp","℃","Num","R","A2"]
[null,null,"水地暖工作压力范围","WaterHeatWorkPressRange","MPa","Numr","M","A6"]
[null,null,"水地暖额定流量","WaterHeatRatedWaterFlow","m3/h","Num","M","A2"]
[null,null,"水地暖管直径","WaterHeatFloorPipeDiameter","mm","Num","R","A2"]
[null,"碳晶地暖设备","碳晶地暖额定电压","CarbonCrystalRatedU","V","Num","S","A2"]
[null,null,"碳晶地暖额定电流","CarbonCrystalRatedI","A","Num","M","A2"]
[null,null,"碳晶地暖电源频率","CarbonCrystalPowerFreq","Hz","Num","M","A2"]
[null,null,"碳晶地暖额定功率","CarbonCrystalRatedP","kW","Num","S","A2"]
[null,null,"碳晶板最高温度","CarbonCrystalMaxTemp","℃","Num","M","A2"]
[null,"发热电缆设备","发热电缆额定电压","CableRatedU","V","Num","S","A2"]
[null,null,"发热电缆额定电流","CableRatedI","A","Num","M","A2"]
[null,null,"发热电缆电源频率","CablePowerFreq","Hz","Num","M","A2"]
[null,null,"发热电缆额定功率","CableRatedP","kW","Num","S","A2"]
[null,null,"发热电缆表面最高温度","CableMaxTemp","℃","Num","M","A2"]
[null,null,"发热电缆线最大载荷","CableMaxLoad","W/m","Num","M","A2"]
[null,null,"发热电缆阻抗","CableImpedance","Ω","Num","R","A2"]
[null,"发热地膜设备","发热地膜额定电压","ThermoelecticFilmRatedU","V","Num","S","A2"]
[null,null,"发热地膜额定电流","ThermoelecticFilmRatedI","A","Num","M","A2"]
[null,null,"发热地膜电源频率","ThermoelecticFilmPowerFreq","Hz","Num","M","A2"]
[null,null,"发热地膜额定功率","ThermoelecticFilmRatedP","kW","Num","S","A2"]
[null,null,"发热地膜最高温度","ThermoelecticFilmMaxTemp","℃","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","M","L"]
[null,null,"供水温度","WaterInTemp","℃","Inst","M","L",null,"水地暖设备"]
[null,null,"回水温度","WaterOutTemp","℃","Inst","M","L",null,"水地暖设备"]
[null,null,"供水压力","WaterInPress","MPa","Inst","R","L",null,"水地暖设备"]
[null,null,"回水压力","WaterOutPress","MPa","Inst","R","L",null,"水地暖设备"]
[null,null,"热水流量","WaterFlow","m3/h","Inst","R","L",null,"水地暖设备"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"碳晶板温度","CarbonCrystalTemp","℃","Inst","M","L",null,"碳晶地暖设备"]
[null,null,"发热电缆温度","CableTemp","℃","Inst","M","L",null,"发热电缆设备"]
[null,null,"电缆线载荷","CableLoad","W/m","Inst","R","L",null,"发热电缆设备"]
[null,null,"发热膜温度","ThermoelecticFilmTemp","℃","Inst","M","L",null,"发热地膜设备"]
[null,"瞬时指标","供热效率","Eff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ATVI变频多联机室内机","index":10,"n_rows":55,"n_cols":10,"rows_kept":55,"cut":false,"hidden":false,"merged":[[48,0,53,1],[54,0,54,1],[39,1,47,1],[0,0,0,9],[1,0,1,1],[2,0,17,1],[18,0,47,0],[18,1,37,1]]}
["室内机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 8. 其他"]
[null,null,"功能模式类型","FuncType",null,"Enum","S","D2","1. 制冷 2. 制热 2. 通风 4. 除湿 5. 其他 （可多选）"]
[null,null,"滤袋个数","FilterNum","个","Num","R","A2"]
[null,null,"额定制冷功率","RatedCoolP","kW","Num","S","A2"]
[null,null,"额定制热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定除湿量","RatedDeD","g/h","Num","M","A2"]
[null,null,"最大电加热功率","MaxElecHeatP","kW","Num","M","A2"]
[null,null,"额定风量","RatedAirFlow","kW","Num","M","A2"]
[null,null,"能效比","RatedCOP",null,"Num","M","A1"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","WorkMode",null,"Enumv","S","L","1. 制冷 2. 制热 3. 通风 4. 除湿 99. 其他"]
[null,null,"工作电压","U","V","Inst","S","L"]
[null,null,"工作频率","Freq","Hz","Inst","S","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","S","L"]
[null,null,"回风温度","ReturnAirTemp","℃","Inst","S","L"]
[null,null,"回风相对湿度","ReturnAirRH","%RH","Inst","M","L"]
[null,null,"送风温度","SupplyAirTemp","℃","Inst","S","L"]
[null,null,"送风相对湿度","SupplyAirRH","%RH","Inst","M","L"]
[null,null,"循环风量","SupplyAirFlow","m3/h","Inst","M","L"]
[null,null,"出口风速","SupplyAirV","m/s","Inst","M","L"]
[null,null,"制冷功率","CoolP","kW","Inst","S","L"]
[null,null,"制热功率","HeatP","kW","Inst","S","L"]
[null,null,"除湿量","DeD","g/h","Inst","M","L"]
[null,null,"电辅热功率","ElecHeatP","kW","Inst","M","L"]
[null,"瞬时指标","COP","COP",null,"Inst","M","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计除湿量","AccDeD","kg","Acc","M","M"]
[null,null,"累计送风量","AccSupplyAir","m3","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp",null,null,"0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump"]
[null,null,"运行模式设定","ModeSet",null,"Enump",null,null,"1. 制冷 2. 制热 3. 通风 4. 除湿 99. 其他"]
[null,null,"室内温度设定","TempSet","℃","Nump"]
[null,null,"出口风速设定","AirSpeedSet",null,"Enump",null,null,"1. 自动 2. 低 3. 中 4. 高 99. 其他"]
[null,null,"摇摆开关设定","SwingSwitchSet",null,"Boolp",null,null,"0. 摇摆关 1. 摇摆开"]
["报警消息"]

{"sheet":"ATVO变频多联机室外机","index":11,"n_rows":38,"n_cols":10,"rows_kept":38,"cut":false,"hidden":false,"merged":[[34,0,36,1],[37,0,37,1],[29,1,33,1],[0,0,0,9],[1,0,1,1],[2,0,17,1],[18,0,33,0],[18,1,27,1]]}
["室外机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"功能模式类型","FuncType",null,"Enum","S","D2","1. 制冷 2. 制热 2. 通风 4. 除湿 99. 其他 （可多选）"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"能效比","RatedCOP",null,"Num","M","A1"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","WorkMode",null,"Enumv","S","L","1. 制冷 2. 制热 3. 通风 4. 除湿 99. 其他"]
[null,null,"工作电压","U","V","Inst","S","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","S","L"]
[null,null,"工作频率","Freq","Hz","Inst","S","L"]
[null,"瞬时指标","COP","COP",null,"Inst","M","M"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp",null,null,"0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump"]
[null,null,"运行模式设定","ModeSet",null,"Enump",null,null,"1. 制冷 2. 制热 3. 通风 4. 除湿 99. 其他"]
["报警消息"]

{"sheet":"ATHD空调加湿器","index":12,"n_rows":35,"n_cols":10,"rows_kept":35,"cut":false,"hidden":false,"merged":[[33,0,33,1],[34,0,34,1],[2,0,18,1],[0,0,0,9],[1,0,1,1],[19,0,32,0],[19,1,27,1],[28,1,32,1]]}
["加湿器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"额定电压","RatedU","V","Num","M","A2"]
[null,null,"额定电流","RatedI","A","Num","R","A2"]
[null,null,"额定功率","RatedP","kW","Num","M","A2"]
[null,null,"加湿器类型","HumidifyType",null,"Enum","S","D1","1. 高压喷雾加湿器 2. 电热式蒸汽加湿器 3. 电极式蒸汽加湿器 4. 干蒸汽加湿器 5. 湿膜加湿器 99. 其他"]
[null,null,"额定加湿量","RatedD","kg/h","Num","S","A2"]
[null,null,"额定处理风量","RatedAirFlow","m3/h","Num","S","A2"]
[null,null,"临界风速","MaxAirV","m/s","Num","M","A2"]
[null,null,"给水温度","RatedWaterInTemp","℃","Num","M","A2"]
[null,null,"给水压力","RatedWaterInPress","MPa","Num","M","A2"]
[null,null,"给水管径","WaterPipeSize","mm","Num","M","A2"]
[null,null,"加湿面积","HumidifyArea","m2","Num","R","A2"]
[null,null,"加湿段长度","HumidifyLength","mm","Num","R","A2"]
[null,null,"饱和加湿效率","SaturatedHumidifyEff","%","Num","M","A2"]
[null,null,"湿膜厚度","WetFilmThick","mm","Num","M","A2",null,"湿膜加湿器"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"加湿量","D","kg/h","Inst","M","L"]
[null,"累计指标","累计加湿量","AccD","kg","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ATMF空调消声器","index":13,"n_rows":18,"n_cols":10,"rows_kept":18,"cut":false,"hidden":false,"merged":[[16,0,16,1],[17,0,17,1],[15,0,15,1],[2,0,14,1],[0,0,0,9],[1,0,1,1]]}
["消声器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"消声器类型","MufflerType",null,"Enum","M","D1","1. 阻性 2. 抗性 3. 阻抗复合式 99. 其他"]
[null,null,"消声频率范围","MuffleFreqRange","Hz","Numr","S","A6"]
[null,null,"最大处理风量","MaxAirFlow","m3/h","Num","S","A2"]
[null,null,"最大处理气流速度","MaxAirV","m/s","Num","M","A2"]
[null,null,"额定处理消声量","RatedMuffle","dB(A)","Num","S","A2"]
[null,null,"阻力系数","ResistCoeff",null,"Num","R","A1"]
[null,null,"通道截面积","SectionArea","m2","Num","R","A2"]
[null,null,"是否有吸声层","isAbsorpLayer",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"吸声层厚度","AbsorpLayerThick","mm","Num","M","A2"]
[null,null,"吸声材料","AbsorpMaterial",null,"Str","R","B1"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作压力范围","WorkPressRange","MPa","Numr","S","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数"]
["设定参数"]
["报警消息"]

{"sheet":"ATPC空调静压箱","index":14,"n_rows":17,"n_cols":10,"rows_kept":17,"cut":false,"hidden":false,"merged":[[15,0,15,1],[16,0,16,1],[13,0,14,1],[2,0,12,1],[0,0,0,9],[1,0,1,1]]}
["静压箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"最大处理风量","MaxAirFlow","m3/h","Num","S","A2"]
[null,null,"最大处理气流速度","MaxAirV","m/s","Num","M","A2"]
[null,null,"阻力系数","ResistCoeff",null,"Num","R","A1"]
[null,null,"通道截面积","SectionArea","m2","Num","R","A2"]
[null,null,"是否有吸声层","isAbsorpLayer",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"吸声层厚度","AbsorpLayerThick","mm","Num","M","A2"]
[null,null,"消声频率范围","MuffleFreqRange","Hz","Numr","S","A6"]
[null,null,"额定处理消声量","RatedMuffle","dB(A)","Num","S","A2"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作压力范围","WorkPressRange","MPa","Numr","S","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"出口静压","AirOutPress","Pa","Inst","M","L"]
[null,null,"瞬时风量","AirFlow","m3/h","Inst","M","L"]
["设定参数"]
["报警消息"]

{"sheet":"ATCA定风量箱","index":15,"n_rows":12,"n_cols":10,"rows_kept":12,"cut":false,"hidden":false,"merged":[[10,0,10,1],[11,0,11,1],[8,0,9,1],[0,0,0,9],[1,0,1,1],[2,0,7,1]]}
["定风量箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"流量精度","FlowAccuracy","%","Num","S","A2"]
[null,null,"额定风量范围","MaxAirFlow","m3/h","Numr","S","A6"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作压力范围","WorkPressRange","MPa","Numr","S","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数",null,"出口静压","AirOutPress","Pa","Inst","M","L"]
[null,null,"瞬时风量","AirFlow","m3/h","Inst","M","L"]
["设定参数"]
["报警消息"]