{"text_format":"2","workbook":"xlsx","n_sheets":5,"sheets":["DWSU生活给水供水机组","DWTS生活给水水箱消毒器","DWUS生活给水紫外线消毒器","DWWT生活给水储水箱","DWPP生活给水水泵"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"DWSU生活给水供水机组","index":0,"n_rows":66,"n_cols":10,"rows_kept":66,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[23,1,31,1],[34,1,36,1],[32,1,33,1],[2,0,36,0],[2,1,22,1],[37,0,60,0],[37,1,54,1],[56,1,60,1],[61,0,63,1],[64,0,65,1]]}
["供水机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"水泵台数","PumpNum","台","Num","S","A2"]
[null,null,"额定供水压力","RatedSupplyPress","MPa","Num","S","A2"]
[null,null,"压力调节精度","PressAdjustPrecision","MPa","Num","R","A2"]
[null,null,"最大供水量","MaxSupplyFlow","m3/h","Num","S","A2"]
[null,null,"是否具有变频功能","isVFD",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"是否具有无负压稳流功能","isNonNegativePressFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"水泵","水泵类型","PumpType",null,"Enum","R","D1","1. 离心泵 2. 柱塞泵 3. 射流泵 4. 螺杆泵 99. 其他"]
[null,null,"额定频率","RatedPumpFreq","Hz","Num","R","A2"]
[null,null,"额定扬程","RatedPumpHead","m","Num","S","A2"]
[null,null,"额定流量","RatedPumpFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedPumpRPM","rpm","Num","M","A2"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","R","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,"变频机组","变频器频率上限","VFDHighLimit","Hz","Num","R","A2"]
[null,null,"变频器频率下限","VFDLowLimit","Hz","Num","R","A2"]
[null,"无负压稳流机组","额定自来水入口水压","RatedTapWaterInPress","MPa","Num","R","A2"]
[null,null,"稳流罐容积","SteadyFlowTankCap","m3","Num","M","A2"]
[null,null,"停水水位","WaterPauseLev","m","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"机组耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"水泵运行台数","PumpRunNum","台","Inst","S","M"]
[null,null,"机组供水流量","WaterFlow","m3/h","Inst","M","L"]
[null,null,"机组进口压力","WaterInPress","MPa","Inst","M","L"]
[null,null,"机组出口压力","WaterOutPress","MPa","Inst","M","L"]
[null,null,"供水扬程","UnitHead","m","Inst","R","M"]
[null,null,"运行频率","UnitFreq","Hz","Inst","M","L",null,"变频机组"]
[null,null,"工作档位","Gear",null,"Enumv","M","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"稳流罐入口水压","SteadyFlowTankInPress","MPa","Inst","M","L",null,"无负压稳流机组"]
[null,null,"稳流罐水位","SteadyFlowTankWaterLev","m","Inst","M","L",null,"无负压稳流机组"]
[null,null,"稳流罐真空度","SteadyFlowTankVacuum","MPa","Inst","R","L",null,"无负压稳流机组"]
[null,"瞬时指标","机组效率","UnitEff","%","Inst","R","M"]
[null,"累计指标","累计供水量","AccSupplyVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum ","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息",null,"超压报警","OverPressAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"供水不足报警","WaterShortAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"DWTS生活给水水箱消毒器","index":1,"n_rows":41,"n_cols":10,"rows_kept":41,"cut":false,"hidden":false,"merged":[[40,0,40,1],[39,0,39,1],[2,1,16,1],[0,0,0,9],[1,0,1,1],[20,0,38,0],[17,1,19,1],[2,0,19,0],[20,1,33,1],[34,1,38,1]]}
["水箱消毒器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","M","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","M","A2"]
[null,null,"额定处理水量（饮用水）","RatedDrinkWaterTreatFlow","m3/h","Num","S","A2"]
[null,null,"额定处理水量（消防水）","RatedFireWaterTreatFlow","m3/h","Num","S","A2"]
[null,null,"水箱长度","TankLength","m","Num","M","A2"]
[null,null,"水箱宽度","TankWidth","m","Num","M","A2"]
[null,null,"水箱高度","TankHeight","m","Num","M","A2"]
[null,null,"水箱容积","TankCap","m3","Num","S","A2"]
[null,null,"安装位置","InstallType",null,"Enum","R","D1","1. 外置式 2. 内置式 99. 其他"]
[null,null,"额定杀菌灭藻率","RatedSterilizeRatio","%","Num","M","A2",null,"原理：强氧化"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,"臭氧发生器","臭氧产量","RatedOzoneGenerateFlow","mol/h","Num","M","A2"]
[null,null,"气源类型","GasSourceType",null,"Enum","R","D1","1. 空气源 2. 氧气源 99. 其他"]
[null,null,"冷却方式","CoolType",null,"Enum","R","D1","1. 风冷 2. 水冷 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"整机耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"处理水流量","TreatFlow","m3/h","Inst","M","L"]
[null,null,"水箱水量","TankWaterVolume","m3","Inst","M","L"]
[null,null,"工作水温","TankWaterTemp","℃","Inst","R","L"]
[null,null,"进口水压","WaterInPress","MPa","Inst","R","L"]
[null,null,"出口水压","WaterOutPress","MPa","Inst","R","L"]
[null,null,"瞬时臭氧产量","OzoneGenerateFlow","mol/h","Inst","R","L"]
[null,"累计指标","累计处理水量","AccTreatVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DWUS生活给水紫外线消毒器","index":2,"n_rows":35,"n_cols":10,"rows_kept":35,"cut":false,"hidden":false,"merged":[[33,0,33,1],[34,0,34,1],[0,0,0,9],[1,0,1,1],[15,0,32,0],[2,0,14,0],[2,1,10,1],[11,1,14,1],[15,1,27,1],[28,1,32,1]]}
["紫外线消毒器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定处理水量","RatedTreatFlow","m3/h","Num","S","A2"]
[null,null,"额定杀菌灭藻率","RatedSterilizeRatio","%","Num","S","A2",null,"原理：强氧化"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,"紫外线发生器","灯管数量","UVLampNum","个","Num","M","A2"]
[null,null,"额定紫外线强度","RatedUVIntensity","W/m2","Num","R","A2"]
[null,null,"进口管径","InPipeDiameter","mm","Num","R","A2"]
[null,null,"出口管径","OutPipeDiameter","mm","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"处理水流量","TreatFlow","m3/h","Inst","M","L"]
[null,null,"工作水温","WaterTemp","℃","Inst","R","L"]
[null,null,"进口水压","WaterInPress","MPa","Inst","R","L"]
[null,null,"出口水压","WaterOutPress","MPa","Inst","R","L"]
[null,null,"紫外线强度","UVIntensity","W/m2","Inst","R","L"]
[null,"累计指标","累计处理水量","AccTreatVolume","m3","Acc","R","M"]
[null,null,"累计耗电功率","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DWWT生活给水储水箱","index":3,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[38,0,39,1],[26,0,36,1],[37,0,37,1],[1,0,1,1],[0,0,0,9],[2,0,25,0],[2,1,19,1],[20,1,22,1],[23,1,25,1]]}
["水箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","内胆","水箱长度","TankLength","m","Num","R","A2"]
[null,null,"水箱宽度","TankWidth","m","Num","R","A2"]
[null,null,"水箱高度","TankHeight","m","Num","R","A2"]
[null,null,"水箱容积","TankCap","m3","Num","S","A2"]
[null,null,"内胆材质","LiningMaterial",null,"Enum","R","D1","1. 不锈钢 2. 搪瓷 3. 塑料 4. 复合材料 99. 其他"]
[null,null,"最大承压","MaxPress","MPa","Num","M","A2"]
[null,null,"底板厚度","BottomBoardThick","mm","Num","R","A2"]
[null,null,"侧板厚度","SideBoardThick","mm","Num","R","A2"]
[null,null,"顶板厚度","TopBoardThick","mm","Num","R","A2"]
[null,null,"进水口截面积","InCrossArea","m2","Num","R","A2"]
[null,null,"出水口截面积","OutCrossArea","m2","Num","R","A2"]
[null,null,"溢流口截面积","OverflowCrossArea","m2","Num","R","A2"]
[null,null,"排污口截面积","SewageCrossArea","m2","Num","R","A2"]
[null,null,"人孔宽度","ManholeWidth","m","Num","R","A2"]
[null,null,"人孔高度","ManholeHeight","m","Num","R","A2"]
[null,null,"内外爬梯高度","LadderHeight","m","Num","R","A2"]
[null,null,"额定水温","RatedWaterTemp","℃","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,"保温层","是否有保温层","isInsulation",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"保温层材料","InsulationMaterial",null,"Enum","R","D1","1. 岩棉 2. 玻璃棉 3. 聚氨酯 4. 聚苯乙烯 5. 酚醛泡沫 99. 其他"]
[null,null,"保温层厚度","InsulationThick","mm","Num","R","A2"]
[null,"外壳","是否有外壳","isShield",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"外壳材质","ShieldMaterial ",null,"Enum","R","D1","1. 不锈钢 2. 塑料 99. 其他"]
[null,null,"外壳抗压强度","ShieldCompressiveStrength","MPa","Num","R","A2"]
["运行参数",null,"水箱水位","TankWaterLev","m","Inst","S","L"]
[null,null,"水箱水量","TankWaterVolume","m3","Inst","R","L"]
[null,null,"水箱水温","TankWaterTemp","℃","Inst","M","L"]
[null,null,"进水流量","WaterInFlow","m3/h","Inst","R","L"]
[null,null,"出水流量","WaterOutFlow","m3/h","Inst","R","L"]
[null,null,"溢流流量","OverflowFlow","m3/h","Inst","R","L"]
[null,null,"排污流量","SewageFlow","m3/h","Inst","R","L"]
[null,null,"进水温度","WaterInTemp","℃","Inst","R","L"]
[null,null,"进水口压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","R","L"]
[null,null,"出水口压力","WaterOutPress","MPa","Inst","R","L"]
["设定参数"]
["报警消息",null,"高液位报警","HighLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"低液位报警","LowLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]

{"sheet":"DWPP生活给水水泵","index":4,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[73,0,76,1],[67,1,72,1],[77,0,77,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"水泵出口压力设定","OutPressSet","MPa","Nump","S","L"]
["报警消息",null,"水泵出口压力低于设定值报警","OutPressUnderSetAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]