{"text_format":"2","workbook":"xlsx","n_sheets":12,"sheets":["DHCB生活热水燃煤锅炉","DHFB生活热水燃油锅炉","DHGB生活热水燃气锅炉","DHEB生活热水电锅炉","DHAH生活热水空气源热泵","DHGH生活热水燃气热水器","DHEH生活热水电热水器","DHSC生活热水太阳能集热器","DHHA生活热水辅热设备","DHHE生活热水换热器","DHHP生活热水水泵","DHWT生活热水储水箱"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"DHCB生活热水燃煤锅炉","index":0,"n_rows":66,"n_cols":10,"rows_kept":66,"cut":false,"hidden":false,"merged":[[62,0,63,1],[64,0,65,1],[54,1,55,1],[56,1,61,1],[0,0,0,9],[1,0,1,1],[2,0,34,0],[25,1,30,1],[31,1,34,1],[19,1,21,1],[22,1,24,1],[35,0,61,0],[35,1,53,1],[2,1,18,1]]}
["燃煤锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"燃煤类型","CoalType",null,"MEnum","R","D2","1. 无烟煤 2. 贫煤 3. 贫瘦煤 4. 瘦煤 5. 焦煤 6. 肥煤 7. 1/3焦煤 8. 气肥煤 9. 气煤 10. 1/2中粘煤 11. 不粘煤 12. 长焰煤 13. 褐煤 99. 其他 （可多选）"]
[null,null,"燃烧方式","BurnType",null,"Enum","M","D1","1. 层燃炉 2. 室燃炉 3. 旋风炉 4. 沸腾燃烧炉 99. 其他"]
[null,null,"除渣方式","DeSlagType",null,"Enum","R","D1","1. 固态除渣炉 2. 液态除渣炉 99. 其他"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定输入燃煤量","RatedCoalConsum","kg/h","Num","S","A2"]
[null,null,"额定工作压力","RatedPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","R","A2",null,"排去的污水量"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"烟气余热\n回收装置","烟气余热回收方式","HeatRecoveryType",null,"Enum","M","D1","1. 预热工件  2. 预热空气  3. 余热回收器（气-水） 4. 余热回收器（气-气）  5. 余热氨水吸收制冷 99. 其他"]
[null,null,"烟气余热回收换热器形式","RecoveryHeatExchangerType",null,"Enum","R","D1","1. 管式 2. 圆筒辐射式 3. 铸铁块状 99. 其他"]
[null,null,"烟气余热回收额定换热量","RatedRecoveryHeatTrans","kW","Num","M","A2"]
[null,null,"烟气余热回收理论换热效率","RatedRecoveryHeatTransEff","%","Num","R","A2"]
[null,null,"烟气余热回收最高工作温度","RecoveryMaxWorkTemp","℃","Num","R","A2"]
[null,null,"烟气余热回收最高工作压力","RecoveryMaxWorkPress","MPa","Num","R","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","M","L"]
[null,null,"燃煤量","CoalConsumP","kg/h","Inst","R","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水锅炉"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"蒸汽压力","VaporOutPress","MPa","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"吸气温度","InAirTemp","℃","Inst","R","L"]
[null,null,"排烟温度","ExhaustSmokeTemp","℃","Inst","M","L"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","M","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","M","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,null,"余热回收效率","HeatRecoveryEff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计燃煤量","AccCoalConsum","kg","Acc","R","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息",null,"排烟温度过高报警","ExhaustSmokeOverTempAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"燃烧器故障报警","BurnerErrorAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"DHFB生活热水燃油锅炉","index":1,"n_rows":66,"n_cols":10,"rows_kept":66,"cut":false,"hidden":false,"merged":[[62,0,63,1],[64,0,65,1],[0,0,0,9],[54,1,55,1],[56,1,61,1],[1,0,1,1],[2,0,32,0],[23,1,28,1],[29,1,32,1],[17,1,19,1],[20,1,22,1],[33,0,61,0],[33,1,53,1],[2,1,16,1]]}
["燃油锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"燃油类型","FuelType",null,"Enum","S","D1","1. 柴油 2. 煤油 3. 重油 99. 其他"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定输入燃油量","RatedFuelConsum","L/h","Num","S","A2"]
[null,null,"额定工作压力","RatedWorkPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","R","A2",null,"排去的污水量"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporOutPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"烟气余热\n回收装置","烟气余热回收方式","HeatRecoveryType",null,"Enum","M","D1","1. 预热工件  2. 预热空气  3. 余热回收器（气-水） 4. 余热回收器（气-气）  5. 余热氨水吸收制冷 99. 其他"]
[null,null,"烟气余热回收换热器形式","RecoveryHeatExchangerType",null,"Enum","R","D1","1. 管式 2. 圆筒辐射式 3. 铸铁块状 99. 其他"]
[null,null,"烟气余热回收额定换热量","RatedRecoveryHeatTrans","kW","Num","M","A2"]
[null,null,"烟气余热回收理论换热效率","RatedRecoveryHeatTransEff","%","Num","R","A2"]
[null,null,"烟气余热回收最高工作温度","RecoveryMaxWorkTemp","℃","Num","R","A2"]
[null,null,"烟气余热回收最高工作压力","RecoveryMaxWorkPress","MPa","Num","R","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","M","L"]
[null,null,"燃油量","FuelConsumP","L/h","Inst","M","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水锅炉"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"蒸汽压力","VaporOutPress","MPa","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"吸气温度","InAirTemp","℃","Inst","R","L"]
[null,null,"排烟温度","ExhaustSmokeTemp","℃","Inst","M","L"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","M","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","M","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,null,"燃油进口压力","FuelInPress","MPa","Inst","R","L"]
[null,null,"燃油阀门开度","FuelValveOpening","%","Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,null,"余热回收效率","HeatRecoveryEff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计燃油量","AccCoalConsum","L","Acc","M","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息",null,"排烟温度过高报警","ExhaustSmokeOverTempAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"燃烧器故障报警","BurnerErrorAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"DHGB生活热水燃气锅炉","index":2,"n_rows":66,"n_cols":10,"rows_kept":66,"cut":false,"hidden":false,"merged":[[62,0,63,1],[64,0,65,1],[0,0,0,9],[54,1,55,1],[56,1,61,1],[1,0,1,1],[2,0,32,0],[23,1,28,1],[29,1,32,1],[17,1,19,1],[20,1,22,1],[33,0,61,0],[33,1,53,1],[2,1,16,1]]}
["燃气锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"燃气类型","GasType",null,"Enum","S","D1","1. 天然气 2. 液化石油气 3. 沼气 4. 城市煤气 99. 其他"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定输入燃气量","RatedGasConsum","m3/h","Num","S","A2"]
[null,null,"额定工作压力","RatedWorkPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","R","A2",null,"排去的污水量"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporOutPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"烟气余热\n回收装置","烟气余热回收方式","HeatRecoveryType",null,"Enum","M","D1","1. 预热工件  2. 预热空气  3. 余热回收器（气-水） 4. 余热回收器（气-气）  5. 余热氨水吸收制冷 99. 其他"]
[null,null,"烟气余热回收换热器形式","RecoveryHeatExchangerType",null,"Enum","R","D1","1. 管式 2. 圆筒辐射式 3. 铸铁块状 99. 其他"]
[null,null,"烟气余热回收额定换热量","RatedRecoveryHeatTrans","kW","Num","M","A2"]
[null,null,"烟气余热回收理论换热效率","RatedRecoveryHeatTransEff","%","Num","R","A2"]
[null,null,"烟气余热回收最高工作温度","RecoveryMaxWorkTemp","℃","Num","R","A2"]
[null,null,"烟气余热回收最高工作压力","RecoveryMaxWorkPress","MPa","Num","R","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","M","L"]
[null,null,"燃气量","GasConsumP","m3/h","Inst","M","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水系统"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水系统"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽系统"]
[null,null,"蒸汽压力","VaporOutPress","MPa","Inst","S","L",null,"蒸汽系统"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"吸气温度","InAirTemp","℃","Inst","R","L"]
[null,null,"排烟温度","ExhaustSmokeTemp","℃","Inst","M","L"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","M","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","M","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,null,"燃气进口压力","GasInPress","MPa","Inst","R","L"]
[null,null,"燃气阀门开度","GasValveOpening","%","Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,null,"余热回收效率","HeatRecoveryEff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计燃气量","AccGasConsum","m3","Acc","M","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息",null,"排烟温度过高报警","ExhaustSmokeOverTempAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"燃烧器故障报警","BurnerErrorAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"DHEB生活热水电锅炉","index":3,"n_rows":65,"n_cols":10,"rows_kept":65,"cut":false,"hidden":false,"merged":[[62,0,63,1],[64,0,64,1],[0,0,0,9],[2,0,31,0],[22,1,24,1],[25,1,27,1],[28,1,31,1],[32,0,61,0],[32,1,54,1],[56,1,61,1],[1,0,1,1],[2,1,21,1]]}
["电锅炉"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","锅炉类型","BoilerType",null,"Enum","S","D1","1. 热水锅炉 2. 蒸汽锅炉 3. 蒸汽热水锅炉 99. 其他"]
[null,null,"安装结构","InstallType",null,"Enum","R","D1","1. 卧式 2. 立式 99. 其他"]
[null,null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定耗电功率","RatedElecConsumP","kW","Num","S","A2"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定工作压力","RatedWorkPress","MPa","Num","M","A2"]
[null,null,"设计热效率","DesignEff","%","Num","M","A2"]
[null,null,"锅炉水容量","WaterCap","t","Num","S","A2"]
[null,null,"额定补水量","RatedFilling","m3/h","Num","M","A2",null,"排去的污水量"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"绝缘等级","InsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"热水锅炉","额定出水温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"额定热水流量","RatedHotWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定受热面发热率","RatedSurfaceHeatRate","kW/m2","Num","M","A2"]
[null,"蒸汽锅炉","额定蒸汽压力","RatedVaporOutPress","MPa","Num","S","A2"]
[null,null,"额定制蒸汽量","RatedVaporFlow","t/h","Num","S","A2"]
[null,null,"额定受热面蒸发率","RatedSurfaceEvaporationRate","t/(hm2)","Num","M","A2"]
[null,"蒸汽冷凝水回收装置","蒸汽冷凝水回收装置是否密闭","isCondensateReturnAirtight",null,"Bool","M","E1","0. 开放式 1. 密闭式"]
[null,null,"蒸汽冷凝水回收最高工作温度","CondensateReturnMaxWorkTemp","℃","Num","R","A2"]
[null,null,"蒸汽冷凝水回收最高工作压力","CondensateReturnMaxWorkPress","MPa","Num","R","A2"]
[null,null,"蒸汽冷凝水回收额定回收量","RatedCondensateReturnFlow","m3/h","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"供热功率","HeatP","kW","Inst","S","L"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","S","L"]
[null,null,"热水循环量","HotWaterFlow","m3/h","Inst","M","L",null,"热水锅炉"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"热水回水温度","HotWaterInTemp","℃","Inst","S","L",null,"热水锅炉"]
[null,null,"制蒸汽量","VaporFlow","t/h","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"蒸汽压力","VaporPress","MPa","Inst","S","L",null,"蒸汽锅炉"]
[null,null,"冷凝水回水温度","VaporCondensateTemp","℃","Inst","R","L",null,"蒸汽锅炉"]
[null,null,"补水阀开度","FillingValveOpening","%","Inst","R","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","R","L"]
[null,null,"冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水PH值","TapWaterPH",null,"Inst","R","L"]
[null,"瞬时指标","锅炉热效率","Eff","%","Inst","R","M"]
[null,"累计指标","累计供热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计补水量","AccFilling","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L",null,"热水锅炉"]
[null,null,"蒸汽压力设定","VaporOutPressSet","MPa","Nump","S","L",null,"蒸汽锅炉"]
["报警消息"]

{"sheet":"DHAH生活热水空气源热泵","index":4,"n_rows":117,"n_cols":10,"rows_kept":117,"cut":false,"hidden":false,"merged":[[113,0,115,1],[116,0,116,1],[0,0,0,9],[106,1,112,1],[1,0,1,1],[2,0,63,0],[44,1,53,1],[54,1,63,1],[64,0,112,0],[64,1,97,1],[98,1,105,1],[2,1,43,1]]}
["空气源热泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"制冷剂类型","RefrigerantType",null,"Enum","M","D1","1. R134a 2. R125 3. R32 4. R143a 5. R22 6. R717(NH3) 7. R744(CO2) 99. 其他"]
[null,null,"制冷剂充注量","RefrigerantCharge","kg","Num","R","A2"]
[null,null,"额定制冷剂循环流量","RatedRefrigerantFlow","m3/h","Num","R","A2"]
[null,null,"额定工况制冷循环图","RatedRefrigerateCycle",null,"Attachment","R","F2"]
[null,null,"是否有四通阀功能","isFourWayValve",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压缩机类型","CompressorType",null,"Enum","M","D1","1. 活塞式 2. 离心式 3. 螺杆式 99. 其他"]
[null,null,"压缩级数","CompressStage","级","Num","R","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1"]
[null,null,"压缩机额定吸气温度","RatedCompressInTemp","℃","Num","R","A2"]
[null,null,"压缩机额定吸气压力","RatedCompressInPress","MPa","Num","R","A2"]
[null,null,"压缩机额定排气温度","RatedCompressOutTemp","℃","Num","R","A2"]
[null,null,"压缩机额定排气压力","RatedCompressOutPress","MPa","Num","R","A2"]
[null,null,"室内侧载冷剂类型","IndoorMeduimType",null,"Enum","S","D1","1. 空气 2. 水 3. 盐水 99. 其他"]
[null,null,"室内侧载冷剂额定流量","RatedIndoorMeduimFlow","m3/h","Num","M","A2"]
[null,null,"室内侧机组换热面积","IndoorHeatTransArea","m2","Num","R","A2"]
[null,null,"室外侧额定风速","RatedOutdoorWindV","m/s","Num","R","A2"]
[null,null,"室外侧机组换热面积","OutdoorHeatTransArea","m2","Num","R","A2"]
[null,null,"室外侧翅片型式","OutdoorFinType",null,"Enum","R","D1","1. 开窗片 2. 波纹片 99. 其他"]
[null,null,"室外侧翅片间距","OutdoorFinGap ","mm","Num","R","A2"]
[null,null,"室外侧布置形式","OutdoorLayoutType",null,"Enum","R","D1","1. 直型 2. V型 3. W型 99. 其他"]
[null,null,"节流阀种类","ValveType",null,"Enum","R","D1","1. 手动膨胀阀 2. 热力膨胀阀 3. 电子膨胀阀 4. 浮球节流阀 5. 节流孔板 6. 毛细管 99. 其他"]
[null,null,"节流级数","ThrottleStage","级","Num","R","A2"]
[null,null,"融霜方式","DefrostType",null,"Enum","R","D1","1. 压差控制法 2. 温差控制法 3. 温度时间控制法 99. 其他","空气侧换热器容易聚霜，一般采用热气除霜，除霜控制技术有所不同"]
[null,null,"安全保护策略","ProtectMode",null,"Str","R","B1"]
[null,null,"压缩机防护等级","CompressIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"压缩机绝缘等级","CompressInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"蒸发器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"蒸发器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"冷凝器耐压试验压力","EvapPunctureTestPress","MPa","Num","M","A2"]
[null,null,"冷凝器最高允许工作压力","EvapMaxAllowPress","MPa","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"制冷工况","额定制冷量","RatedCool","kW","Num","S","A2"]
[null,null,"额定制冷COP","RatedCoolCOP",null,"Num","M","A1"]
[null,null,"制冷工况室内侧设计机组入口载冷剂温度","DesignCoolIndoorMediumInTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况室内侧设计机组出口载冷剂温度","DesignCoolIndoorMediumOutTemp","℃","Num","M","A2",null,"蒸发器"]
[null,null,"制冷工况额定蒸发温度","RatedCoolEvapTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定蒸发压力","RatedCoolEvapPress","MPa","Num","R","A2"]
[null,null,"制冷工况室外侧设计机组入口空气温度","DesignCoolOutdoorAirInTemp","℃","Num","R","A2",null,"冷凝器"]
[null,null,"制冷工况室外侧设计机组出口空气温度","DesignCoolOutdoorAirOutTemp","℃","Num","R","A2",null,"冷凝器"]
[null,null,"制冷工况额定冷凝温度","RatedCoolCondTemp","℃","Num","R","A2"]
[null,null,"制冷工况额定冷凝压力","RatedCoolCondPress","MPa","Num","R","A2"]
[null,"制热工况","额定制热量","RatedHeat","kW","Num","S","A2"]
[null,null,"额定制热COP","RatedHeatCOP",null,"Num","M","A1"]
[null,null,"制热工况室内侧设计机组入口载冷剂温度","DesignHeatIndoorMediumInTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况室内侧设计机组出口载冷剂温度","DesignHeatIndoorMediumOutTemp","℃","Num","M","A2",null,"冷凝器"]
[null,null,"制热工况额定冷凝温度","RatedHeatCondTemp","℃","Num","R","A2"]
[null,null,"制热工况额定冷凝压力","RatedHeatCondPress","MPa","Num","R","A2"]
[null,null,"制热工况室外侧设计机组入口空气温度","DesignHeatOutdoorAirInTemp","℃","Num","R","A2",null,"蒸发器"]
[null,null,"制热工况室外侧设计机组出口空气温度","DesignHeatOutdoorAirOutTemp","℃","Num","R","A2",null,"蒸发器"]
[null,null,"制热工况额定蒸发温度","RatedHeatEvapTemp","℃","Num","R","A2"]
[null,null,"制热工况额定蒸发压力","RatedHeatEvapPress","MPa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"运行模式","RunMode",null,"Enumv","S","L","1. 制冷 2. 制热 99. 其他"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","S","L",null,"三相有功功率"]
[null,null,"瞬时制冷量","CoolP","kW","Inst","S","L"]
[null,null,"瞬时制热量","HeatP","kW","Inst","S","L"]
[null,null,"工作频率","WorkFreq","Hz","Inst","R","L",null,"有变频功能时"]
[null,null,"室内侧机组入口载冷剂温度","IndoorMediumInTemp","℃","Inst","S","L"]
[null,null,"室内侧机组出口载冷剂温度","IndoorMediumOutTemp","℃","Inst","S","L"]
[null,null,"室内侧机组入口载冷剂压力","IndoorMediumInPress","MPa","Inst","R","L"]
[null,null,"室内侧机组出口载冷剂压力","IndoorMediumOutPress","MPa","Inst","R","L"]
[null,null,"室内侧载冷剂流量","IndoorMediumFlow","m3/h","Inst","M","L"]
[null,null,"压缩机吸气温度","CompressInTemp","℃",null,null,"L"]
[null,null,"压缩机吸气压力","CompressInPress","MPa",null,null,"L"]
[null,null,"压缩机排气温度","CompressOutTemp","℃",null,null,"L"]
[null,null,"压缩机排气压力","CompressOutPress","MPa",null,null,"L"]
[null,null,"室外侧机组入口空气温度","OutdoorAirInTemp","℃","Inst","M","L"]
[null,null,"室外侧机组出口空气温度","OutdoorAirOutTemp","℃","Inst","M","L"]
[null,null,"室外侧机组入口空气压力","OutdoorAirInPress","Pa","Inst","R","L"]
[null,null,"室外侧机组出口空气压力","OutdoorAirOutPress","Pa","Inst","R","L"]
[null,null,"室外侧风速","OutdoorWindV","m/s","Inst","R","L"]
[null,null,"蒸发温度","EvapTemp","℃","Inst","M","L"]
[null,null,"蒸发压力","EvapPress","MPa","Inst","M","L"]
[null,null,"冷凝温度","CondTemp","℃","Inst","M","L"]
[null,null,"冷凝压力","CondPress","MPa","Inst","M","L"]
[null,"瞬时指标","热泵负载率","PLR","%","Inst","R","M",null,"实际供冷（热）量/额定供冷（热）量"]
[null,null,"电流负载率","IPLR","%","Inst","M","M",null,"实际电流/额定电流"]
[null,null,"热不平衡率","HeatUnbalanceRate","%","Inst","R","M",null,"（冷凝热量-制冷量-功率）/制冷量"]
[null,null,"COP","COP",null,"Inst","M","M",null,"总体效率（DCOP×ICOP）"]
[null,null,"DCOP","DCOP",null,"Inst","R","M",null,"内部效率"]
[null,null,"ICOP","ICOP",null,"Inst","R","M",null,"外部效率"]
[null,null,"蒸发器过热度","EvapSuperheat","℃","Inst","R","M"]
[null,null,"冷凝器过冷度","CondSupercool","℃","Inst","R","M"]
[null,"累计指标","累计制冷量","AccCool","kWh","Acc","M","M"]
[null,null,"累计制热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"IPLV","IPLV",null,"Inst","R","M",null,"部分负荷性能系数"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"热水出水温度设定","HotWaterOutTempSet","℃","Nump","S","L"]
["报警消息"]

{"sheet":"DHGH生活热水燃气热水器","index":5,"n_rows":55,"n_cols":10,"rows_kept":55,"cut":false,"hidden":false,"merged":[[53,0,53,1],[54,0,54,1],[0,0,0,9],[1,0,1,1],[25,0,52,0],[2,0,24,1],[25,1,45,1],[47,1,52,1]]}
["燃气热水器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"安装结构","InstallType",null,"Enum","M","D1","1. 壁挂式 2. 立式 99. 其他"]
[null,null,"燃气类型","GasType",null,"Enum","S","D1","1. 天然气 2. 液化石油气 3. 沼气 4. 城市煤气 99. 其他"]
[null,null,"点火方式","IgniteType",null,"Enum","R","D1","1. 电子脉冲点火 2. 水控全自动电脉冲点火 99. 其他"]
[null,null,"排风类型","ExhaustSmokeType",null,"Enum","R","D1","1. 烟道式 2. 强排式 3. 平衡式 99. 其他"]
[null,null,"额定电压","RatedU","V","Num","R","A2"]
[null,null,"额定电流","RatedI","A","Num","R","A2"]
[null,null,"额定耗电功率","RatedElecConsumP","kW","Num","R","A2"]
[null,null,"额定输入燃气量","RatedGasConsum","m3/h","Num","S","A2"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定出水温度","RatedOutTemp","℃","Num","S","A2"]
[null,null,"额定出水流量","RatedOutFlow","m3/h","Num","S","A2"]
[null,null,"额定出水压力","RatedOutPress","MPa","Num","M","A2"]
[null,null,"内胆贮水量","LiningWaterCap","L","Num","M","A2"]
[null,null,"额定复热水量","RatedReheatWaterCap","L","Num","R","A2",null,"指在使用热水的时间内重新加热的热水量"]
[null,null,"额定复热率","RatedReheatFlow","L/h","Num","R","A2",null,"指单位时间里重新加热热水量的多少"]
[null,null,"供热水量","RatedSupplyHotWaterCap","L","Num","S","A2",null,"供热水量为原内胆的贮水量与复热水量之和"]
[null,null,"设计热效率","DesignHeatEff","%","Num","R","A2"]
[null,null,"温度设定范围","SetTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"加热功率","HeatP","kW","Inst","R","L"]
[null,null,"燃气量","GasConsumFlow","m3/h","Inst","R","L"]
[null,null,"热水阀开度","HotWaterValveOpening","%","Inst","M","L"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","M","L"]
[null,null,"热水出水流量","HotWaterOutFlow","m3/h","Inst","R","L"]
[null,null,"热水出水压力","HotWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷水阀开度","TapWaterValveOpening","%","Inst","M","L"]
[null,null,"冷水出水温度","TapWaterOutTemp","℃","Inst","M","L"]
[null,null,"冷水出水流量","TapWaterOutFlow","m3/h","Inst","R","L"]
[null,null,"冷水出水压力","TapWaterOutPress","MPa","Inst","R","L"]
[null,null,"混合出水温度","MixWaterOutTemp","℃","Inst","M","L"]
[null,null,"混合出水流量","MixWaterOutFlow","m3/h","Inst","R","L"]
[null,null,"混合出水压力","MixWaterOutPress","MPa","Inst","R","L"]
[null,null,"排烟温度","ExhaustSmokeTemp","℃","Inst","M","L"]
[null,null,"燃气进口压力","GasInPress","MPa","Inst","R","L"]
[null,null,"燃气阀门开度","GasValveOpening","%","Inst","R","L"]
[null,"瞬时指标","热效率","HeatEff","%","Inst","R","M"]
[null,"累计指标","累计出水量","AccSupplyVolume","m3","Acc","R","M"]
[null,null,"累计加热量","AccHeat ","kWh","Acc","R","M"]
[null,null,"累计燃气量","AccGasConsum","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DHEH生活热水电热水器","index":6,"n_rows":53,"n_cols":10,"rows_kept":53,"cut":false,"hidden":false,"merged":[[51,0,51,1],[52,0,52,1],[1,0,1,1],[0,0,0,9],[24,0,50,0],[24,1,43,1],[45,1,50,1],[2,0,23,1]]}
["电热水器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"安装结构","InstallType",null,"Enum","M","D1","1. 壁挂式 2. 立式 99. 其他"]
[null,null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定耗电功率","RatedElecConsumP","kW","Num","S","A2"]
[null,null,"额定加热功率","RatedHeatP","kW","Num","S","A2"]
[null,null,"额定出水温度","RatedOutTemp","℃","Num","S","A2"]
[null,null,"额定出水流量","RatedOutFlow","m3/h","Num","S","A2"]
[null,null,"额定出水压力","RatedOutPress","MPa","Num","M","A2"]
[null,null,"内胆贮水量","LiningWaterCap","L","Num","M","A2"]
[null,null,"额定复热水量","RatedReheatWaterCap","L","Num","R","A2",null,"指在使用热水的时间内重新加热的热水量"]
[null,null,"额定复热率","RatedReheatFlow","L/h","Num","R","A2",null,"指单位时间里重新加热热水量的多少"]
[null,null,"供热水量","RatedHotWaterSupplyCap","L","Num","S","A2",null,"供热水量为原内胆的贮水量与复热水量之和"]
[null,null,"设计热效率","DesignHeatEff","%","Num","R","A2"]
[null,null,"温度设定范围","SetTempRange","℃","Numr","M","A6"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"绝缘等级","InsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"加热功率","HeatP","kW","Inst","S","L"]
[null,null,"工作电压","U","V","Inst","S","L"]
[null,null,"工作电流","I","A","Inst","S","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","S","L"]
[null,null,"热水阀开度","HotWaterValveOpening","%","Inst","M","L"]
[null,null,"热水出水温度","HotWaterOutTemp","℃","Inst","M","L"]
[null,null,"热水出水流量","HotWaterOutFlow","m3/h","Inst","R","L"]
[null,null,"热水出水压力","HotWaterOutPress","MPa","Inst","R","L"]
[null,null,"冷水阀开度","TapWaterValveOpening","%","Inst","M","L"]
[null,null,"冷水出水温度","TapWaterOutTemp","℃","Inst","M","L"]
[null,null,"冷水出水流量","TapWaterOutFlow","m3/h","Inst","R","L"]
[null,null,"冷水出水压力","TapWaterOutPress","MPa","Inst","R","L"]
[null,null,"混合出水温度","MixWaterOutTemp","℃","Inst","M","L"]
[null,null,"混合出水流量","MixWaterOutFlow","m3/h","Inst","R","L"]
[null,null,"混合出水压力","MixWaterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","热效率","HeatEff","%","Inst","R","M"]
[null,"累计指标","累计出水量","AccSupplyVolume","m3","Acc","R","M"]
[null,null,"累计加热量","AccHeat ","kWh","Acc","R","M"]
[null,null,"累计耗电量","AccGasConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DHSC生活热水太阳能集热器","index":7,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[38,0,38,1],[39,0,39,1],[34,1,37,1],[0,0,0,9],[1,0,1,1],[2,0,21,0],[2,1,6,1],[7,1,10,1],[11,1,12,1],[14,1,21,1],[22,0,37,0],[22,1,32,1]]}
["太阳能集热器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","集热板","集热板材质","CollectPlateMaterial",null,"Enum","R","D1","1. 铜 2. 铝合金 3. 铜铝复合 4. 不锈钢 5. 镀锌钢 6. 塑料 7. 橡胶 99. 其他"]
[null,null,"集热板形式","CollectPlateType",null,"Enum","R","D1","1. 管板式 2. 翼管式 3. 蛇管式 4. 扁盒式 99. 其他"]
[null,null,"吸收涂层类型","AbsorbCoatType",null,"Enum","R","D1","1. 电镀涂层（黑铬涂层、黑镍涂层、黑钴涂层） 2. 电化学表面转化涂层（铝阳极氧化涂层、CuO转化涂层） 3. 真空镀涂层 99. 其他"]
[null,null,"吸收率","Absorptivity","%","Num","R","A2"]
[null,null,"发射率","Emissivity","%","Num","R","A2"]
[null,"盖板","盖板材质","CoverPlateMaterial",null,"Enum","R","D1","1. 平板玻璃 2. 玻璃钢板 99. 其他"]
[null,null,"盖板长度","CoverPlateLength","mm","Num","R","A2"]
[null,null,"盖板宽度","CoverPlateWidth","mm","Num","R","A2"]
[null,null,"盖板透光率","CoverPlateTransmittance","%","Num","R","A2"]
[null,"保温层","保温层材质","InsulationMaterial",null,"Enum","R","D1","1. 岩棉 2. 玻璃棉 3. 聚氨酯 4. 聚苯乙烯 5. 酚醛泡沫 99. 其他"]
[null,null,"保温层厚度","InsulationThick","mm","Num","R","A2"]
[null,"外壳","外壳材质","ShieldMaterial",null,"Enum","R","D1","1. 铝合金 2. 不锈钢板 3. 碳钢板 4. 塑料 5. 玻璃钢 99. 其他"]
[null,"性能","集热板总面积","CollectPlateArea","m2","Num","S","A2"]
[null,null,"有效吸热面积","EffectiveAbsorbArea","m2","Num","R","A2"]
[null,null,"额定集热功率","RatedCollectHeatP","kW","Num","S","A2"]
[null,null,"最大工作压力","MaxWorkPress","MPa","Num","M","A2"]
[null,null,"空晒最高温度","MaxDryStagnationTemp","℃","Num","M","A2",null,"以空气为工质，除出口的配管接口敞开作排气外，别的接口均用堵头密封"]
[null,null,"加水闷晒最高温度","MaxWaterStagnationTemp","℃","Num","M","A2",null,"依照在室外运行时的倾角和方向装置，集热器内充溢传热工质水并被阳光加热至当天最高温度"]
[null,null,"加防冻液闷晒最高温度","MaxAntifreezeStagnationTemp","℃","Num","M","A2",null,"依照在室外运行时的倾角和方向装置，集热器内充溢传热工质防冻液并被阳光加热至当天最高温度"]
[null,null,"耐冻性","FreezeResistance","℃","Num","M","A2",null,"加防冻液后可以使用的最低温度"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,null,null,"L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"进口水温","WaterInTemp","℃","Inst","S","L"]
[null,null,"进口压力","WaterInPress","MPa","Inst","M","L"]
[null,null,"出口水温","WaterOutTemp","℃","Inst","S","L"]
[null,null,"出口压力","WaterOutPress","MPa","Inst","M","L"]
[null,null,"水流量","WaterFlow","m3/h","Inst","M","L"]
[null,null,"表面温度","SurfaceTemp","℃","Inst","R","L"]
[null,"瞬时指标","集热效率","CollectHeatEff","%","Inst","R","M"]
[null,"累计指标","累计集热量","AccCollectHeat","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime ","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DHHA生活热水辅热设备","index":8,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[2,0,16,0],[2,1,6,1],[7,1,11,1],[12,1,16,1],[17,0,37,0],[17,1,30,1],[32,1,37,1],[38,0,38,1],[39,0,39,1]]}
["辅热设备"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","辅助热源类型","AuxiliaryHeatType",null,"Enum","S","D1","1. 市政热力管网 2. 电加热 3. 燃油锅炉 4. 燃气锅炉 5. 电锅炉 6. 水源热泵 7. 地源热泵 8. 空气源热泵 99. 其他"]
[null,null,"热水额定出口温度","RatedHotWaterOutTemp","℃","Num","S","A2"]
[null,null,"热水额定流量","RatedHotWaterFlow","m3/h","Num","M","A2"]
[null,null,"热水额定进口压力","RatedHotWaterInPress","MPa","Num","R","A2"]
[null,null,"热水额定出口压力","RatedHotWaterOutPress","MPa","Num","R","A2"]
[null,"电加热","电加热额定电压","RatedU","V","Num","S","A2"]
[null,null,"电加热额定电流","RatedI","A","Num","M","A2"]
[null,null,"电加热额定耗电功率","RatedElecConsumP","kW","Num","S","A2"]
[null,null,"电加热最大加热功率","MaxElecHeatP","kW","Num","S","A2"]
[null,null,"额定电加热效率","RatedElecHeatEff","%","Num","R","A2"]
[null,"换热器","换热器热媒类型","HeatMediumType",null,"Enum","M","D1","1. 水 2. 酒精 99. 其他"]
[null,null,"换热器换热面积","HeatTransArea","m2","Num","R","A2"]
[null,null,"换热器设计传热系数","DesignTransFactor","W/(m2K)","Num","R","A2"]
[null,null,"换热器最大加热功率","MaxTransHeatP","kW","Num","R","A2"]
[null,null,"设计换热效率","DesignTransHeatEff","%","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"加热功率","HeatP","kW","Inst","M","L"]
[null,null,"进口水温","WaterInTemp","℃","Inst","M","L"]
[null,null,"进口压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出口水温","WaterOutTemp","℃","Inst","M","L"]
[null,null,"出口压力","WaterOutPress","MPa","Inst","R","L"]
[null,null,"热水流量","WaterFlow","m3/h","Inst","R","L"]
[null,"瞬时指标","加热效率","HeatEff","%","Inst","R","M"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计水流量","AccWaterVolume","m3","Acc","R","M"]
[null,null,"累计加热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime ","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DHHE生活热水换热器","index":9,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":false,"merged":[[0,0,0,9],[42,0,42,1],[43,0,43,1],[1,0,1,1],[39,1,41,1],[2,0,16,1],[17,0,41,0],[17,1,38,1]]}
["换热器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"换热介质类型","MediumType",null,"Enum","S","D1","1. 水-水换热 2. 水-汽换热 99. 其他"]
[null,null,"结构类型","StructureType",null,"Enum","M","D1","1. 夹套式换热器 2. 蛇管式换热器 3. 套管式换热器 4. 列管式换热器 5. 板片式换热器 6. 非金属换热器 99. 其他"]
[null,null,"设计换热量","DesignHeatTrans","kW","Num","M","A2"]
[null,null,"换热面积","HeatTransArea","m2","Num","R","A2"]
[null,null,"高温侧设计水流量","DesignHighFlow","m3/h","Num","R","A2"]
[null,null,"高温侧设计进水温度","DesignHighInTemp","℃","Num","R","A2"]
[null,null,"高温侧设计出水温度","DesignHighOutTemp","℃","Num","R","A2"]
[null,null,"高温侧设计供蒸汽压力","DesignHighVaporPress","MPa","Num","R","A2",null,"水-汽换热时"]
[null,null,"高温侧设计供蒸汽流量","DesignHighVaporFlow","t/h","Num","R","A2",null,"水-汽换热时"]
[null,null,"低温侧设计水流量","DesignLowFlow","m3/h","Num","R","A2"]
[null,null,"低温侧设计进水温度","DesignLowInTemp","℃","Num","R","A2"]
[null,null,"低温侧设计出水温度","DesignLowOutTemp","℃","Num","R","A2"]
[null,null,"传热系数","HeatTransCoeff","W/(m2K)","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"换热功率","HeatTransP","kW","Inst","R","L"]
[null,null,"高温侧进水温度","HighInTemp","℃","Inst","S","L"]
[null,null,"高温侧出水温度","HighOutTemp","℃","Inst","S","L"]
[null,null,"高温侧水阀开度","HighValveOpening","%","Inst","R","L"]
[null,null,"高温侧瞬时流量","HighFlow","m3/h","Inst","M","L"]
[null,null,"高温侧进水压力","HighInPress","MPa","Inst","R","L"]
[null,null,"高温侧出水压力","HighOutPress","MPa","Inst","R","L"]
[null,null,"高温侧供蒸汽压力","HighVaporPress","MPa","Inst","S","L",null,"水-汽换热时"]
[null,null,"高温侧凝水温度","HighCondenseWaterTemp","℃","Inst","M","L",null,"水-汽换热时"]
[null,null,"高温侧蒸汽阀开度","HighVaporValveOpening","%","Inst","R","L",null,"水-汽换热时"]
[null,null,"高温侧瞬时蒸汽流量","HighVaporFlow","t/h","Inst","M","L",null,"水-汽换热时"]
[null,null,"低温侧进水温度","LowInTemp","℃","Inst","S","L"]
[null,null,"低温侧出水温度","LowOutTemp","℃","Inst","S","L"]
[null,null,"低温侧水阀状态","LowValveOpening","%","Inst","R","L"]
[null,null,"低温侧瞬时流量","LowFlow","m3/h","Inst","M","L"]
[null,null,"低温侧进水压力","LowInPress","MPa","Inst","R","L"]
[null,null,"低温侧出水压力","LowOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","换热器高温侧阻力","HighResistance","MPa","Inst","R","M"]
[null,null,"换热器低温侧阻力","LowResistance","MPa","Inst","R","M"]
[null,null,"换热效率","HeatTransEff","%","Inst","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DHHP生活热水水泵","index":10,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[77,0,77,1],[67,1,72,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1],[73,0,76,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"水泵出口压力设定","OutPressSet","MPa","Nump","S","L"]
["报警消息",null,"水泵出口压力低于设定值报警","OutPressUnderSetAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"DHWT生活热水储水箱","index":11,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[38,0,39,1],[26,0,36,1],[37,0,37,1],[1,0,1,1],[0,0,0,9],[2,0,25,0],[2,1,19,1],[20,1,22,1],[23,1,25,1]]}
["水箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","内胆","水箱长度","TankLength","m","Num","R","A2"]
[null,null,"水箱宽度","TankWidth","m","Num","R","A2"]
[null,null,"水箱高度","TankHeight","m","Num","R","A2"]
[null,null,"水箱容积","TankCap","m3","Num","S","A2"]
[null,null,"内胆材质","LiningMaterial",null,"Enum","R","D1","1. 不锈钢 2. 搪瓷 3. 塑料 4. 复合材料 99. 其他"]
[null,null,"最大承压","MaxPress","MPa","Num","M","A2"]
[null,null,"底板厚度","BottomBoardThick","mm","Num","R","A2"]
[null,null,"侧板厚度","SideBoardThick","mm","Num","R","A2"]
[null,null,"顶板厚度","TopBoardThick","mm","Num","R","A2"]
[null,null,"进水口截面积","InCrossArea","m2","Num","R","A2"]
[null,null,"出水口截面积","OutCrossArea","m2","Num","R","A2"]
[null,null,"溢流口截面积","OverflowCrossArea","m2","Num","R","A2"]
[null,null,"排污口截面积","SewageCrossArea","m2","Num","R","A2"]
[null,null,"人孔宽度","ManholeWidth","m","Num","R","A2"]
[null,null,"人孔高度","ManholeHeight","m","Num","R","A2"]
[null,null,"内外爬梯高度","LadderHeight","m","Num","R","A2"]
[null,null,"额定水温","RatedWaterTemp","℃","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,"保温层","是否有保温层","isInsulation",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"保温层材料","InsulationMaterial",null,"Enum","R","D1","1. 岩棉 2. 玻璃棉 3. 聚氨酯 4. 聚苯乙烯 5. 酚醛泡沫 99. 其他"]
[null,null,"保温层厚度","InsulationThick","mm","Num","R","A2"]
[null,"外壳","是否有外壳","isShield",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"外壳材质","ShieldMaterial ",null,"Enum","R","D1","1. 不锈钢 2. 塑料 99. 其他"]
[null,null,"外壳抗压强度","ShieldCompressiveStrength","MPa","Num","R","A2"]
["运行参数",null,"水箱水位","TankWaterLev","m","Inst","S","L"]
[null,null,"水箱水量","TankWaterVolume","m3","Inst","R","L"]
[null,null,"水箱水温","TankWaterTemp","℃","Inst","M","L"]
[null,null,"进水流量","WaterInFlow","m3/h","Inst","R","L"]
[null,null,"出水流量","WaterOutFlow","m3/h","Inst","R","L"]
[null,null,"溢流流量","OverflowFlow","m3/h","Inst","R","L"]
[null,null,"排污流量","SewageFlow","m3/h","Inst","R","L"]
[null,null,"进水温度","WaterInTemp","℃","Inst","R","L"]
[null,null,"进水口压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","R","L"]
[null,null,"出水口压力","WaterOutPress","MPa","Inst","R","L"]
["设定参数"]
["报警消息",null,"高液位报警","HighLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"低液位报警","LowLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]