{"text_format":"2","workbook":"xlsx","n_sheets":2,"sheets":["DDTU直饮水处理机组","DDIH直饮水即时加热器"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"DDTU直饮水处理机组","index":0,"n_rows":75,"n_cols":10,"rows_kept":75,"cut":false,"hidden":false,"merged":[[73,0,73,1],[74,0,74,1],[0,0,0,9],[1,0,1,1],[26,1,34,1],[47,0,72,0],[17,1,25,1],[35,1,40,1],[41,1,42,1],[43,1,45,1],[68,1,72,1],[47,1,64,1],[65,1,67,1],[2,0,46,0],[2,1,16,1]]}
["直饮水处理机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"机组额定总功率","RatedP","kW","Num","S","A2"]
[null,null,"最大出水流量","MaxWaterOutFlow","m3/h","Num","S","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"加压泵","加压泵类型","PressPumpType",null,"Enum","R","D1","1. 离心泵 2. 柱塞泵 3. 射流泵 4. 螺杆泵 99. 其他"]
[null,null,"加压泵额定频率","PressPumpRatedFreq","Hz","Num","R","A2"]
[null,null,"加压泵额定扬程","PressPumpRatedHead","m","Num","S","A2"]
[null,null,"加压泵额定流量","PressPumpRatedFlow","m3/h","Num","S","A2"]
[null,null,"加压泵额定转速","PressPumpRatedRPM","rpm","Num","M","A2"]
[null,null,"加压泵直径","PressPumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"加压泵电机额定效率","PressPumpMotorRatedEff","%","Num","R","A2"]
[null,null,"加压泵额定效率","PressPumpRatedEff","%","Num","R","A2"]
[null,null,"加压泵特性曲线","PressPumpCharacterCurve",null,"Attachment","R","F1"]
[null,"过滤器","过滤器介质","FilterMediumType",null,"Enum","R","D1","1. 永久性（石英砂） 2. 半永久性（聚脂纤维过滤芯、活性炭、浮石） 3. 短期（硅藻土） 99. 其他"]
[null,null,"过滤器设计滤速","FilterDesignV","m/s","Num","R","A2"]
[null,null,"过滤器滤层数","FilterLayerNum","层","Num","R","A2"]
[null,null,"过滤器滤层充填高度","FilterLayerHeight","mm","Num","R","A2"]
[null,null,"过滤器理论出水浊度","FilterRatedOutTurbidity","mg/L","Num","R","A2"]
[null,null,"过滤器理论过滤效率","FilterRatedEff","%","Num","M","A2"]
[null,null,"过滤器水反洗强度","FilterBackwashIntensity","L/s","Num","R","A2"]
[null,null,"过滤器反洗间隔","FilterBackwashInterval","h","Num","R","A2"]
[null,null,"过滤器反洗时间","FilterBackwashTime","min","Num","R","A2"]
[null,"软化器","软化器进口管径","SoftenerInPipeDiameter","mm","Num","R","A2"]
[null,null,"软化器出口管径","SoftenerOutPipeDiameter","mm","Num","R","A2"]
[null,null,"软化器排污管直径","SoftenerSewagePipeDiameter","mm","Num","R","A2"]
[null,null,"软化器周期产水量","SoftenerPeriodTreatWaterCap","m3","Num","M","A2"]
[null,null,"软化器再生周期","SoftenerRegeneratePeriod","h","Num","R","A2"]
[null,null,"软化器再生剂额定储量","SoftenerRatedRegenerantStore","L","Num","R","A2"]
[null,"反渗透","反渗透额定产水量","RORatedWaterGenerateFlow","m3/h","Num","M","A2"]
[null,null,"反渗透额定脱盐率","RORatedDesaltRate","%","Num","R","A2"]
[null,"臭氧发生器","臭氧发生器额定产量","OzoneRatedGenerateFlow","mol/h","Num","R","A2"]
[null,null,"臭氧发生器额定杀菌率","OzoneRatedSterilizeRate","%","Num","M","A2"]
[null,null,"臭氧发生器额定处理速率","OzoneRatedTreatFlow","m3/h","Num","R","A2"]
[null,"储水箱","储水箱容积","DrinkWaterTankCap","m3","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"机组耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"机组进水压力","WaterInPress","MPa","Inst","M","L"]
[null,null,"机组出水压力","WaterOutPress","MPa","Inst","M","L"]
[null,null,"直饮水出水流量","DrinkWaterOutFlow","m3/h","Inst","M","L"]
[null,null,"直饮水出水温度","DrinkWaterOutTemp","℃","Inst","M","L"]
[null,null,"直饮水当前储水量","DrinkWaterStoreVolume","m3","Inst","M","L"]
[null,null,"直饮水硬度","DrinkWaterOutHardness","mg/L","Inst","R","L"]
[null,null,"直饮水PH值","DrinkWaterOutPH",null,"Inst","R","L"]
[null,null,"直饮水SS值","DrinkWaterOutSS","mg/L","Inst","R","L",null,"悬浮物小于70，需要不定时取样检测"]
[null,null,"直饮水COD值","DrinkWaterOutCOD","mg/L","Inst","R","L",null,"化学需氧量小于100，需要不定时取样检测"]
[null,null,"臭氧产量","OzoneGenerateFlow","mol/h","Inst","R","L"]
[null,null,"再生剂储量","RegenerantStore","L","Inst","R","L"]
[null,"瞬时指标","杀菌率","SterilizeRate","%","Inst","R","M",null,"需要不定时取样检测"]
[null,null,"过滤效率","FiltEff","%","Inst","R","M",null,"需要不定时取样检测"]
[null,null,"脱盐率","DesaltRate","%","Inst","R","M",null,"需要不定时取样检测"]
[null,"累计指标","累计供水量","AccSupplyWaterVolume","m3","Acc","M","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DDIH直饮水即时加热器","index":1,"n_rows":38,"n_cols":10,"rows_kept":38,"cut":false,"hidden":false,"merged":[[36,0,36,1],[37,0,37,1],[0,0,0,9],[1,0,1,1],[15,0,35,0],[15,1,28,1],[30,1,35,1],[2,0,14,1]]}
["即时加热器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定耗电功率","RatedP","kW","Num","S","A2"]
[null,null,"最大加热功率","MaxHeatP","kW","Num","S","A2"]
[null,null,"设计水流量","DesignWaterFlow","m3/h","Num","S","A2"]
[null,null,"加热器形式","HeaterType",null,"Enum","M","D1","1. 集中加热式 2. 分散加热式 99. 其他"]
[null,null,"额定加热效率","RatedHeatEff","%","Num","R","A2"]
[null,null,"设定温度范围","SetTempRange","℃","Numr","S","A6"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"绝缘等级","InsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"加热功率","HeatP","kW","Inst","M","L"]
[null,null,"当前水流量","WaterFlow","m3/h","Inst","R","L"]
[null,null,"进水温度","WaterInTemp","℃","Inst","M","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","M","L"]
[null,null,"进水压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出水压力","WaterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","加热效率","HeatEff","%","Inst","R","M"]
[null,"累计指标","累计供水量","AccSupplyWaterVolume","m3","Acc","R","M"]
[null,null,"累计加热量","AccHeat","kWh","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]