{"text_format":"2","workbook":"xlsx","n_sheets":5,"sheets":["WSCF水景循环过滤机组","WSSN水景喷头","WSCU水景控制箱","WSLT水景灯具","WSPP水景水泵"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"WSCF水景循环过滤机组","index":0,"n_rows":68,"n_cols":10,"rows_kept":68,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[25,1,33,1],[2,0,42,0],[2,1,24,1],[64,0,66,1],[67,0,67,1],[43,0,63,0],[58,1,63,1],[34,1,42,1],[43,1,56,1]]}
["水景循环过滤机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定处理水量","RatedTreatFlow","m3/h","Num","S","A2"]
[null,null,"最大处理水量","MaxTreatFlow","m3/h","Num","S","A2"]
[null,null,"水景池有效容积","ScapeBasinCap","m3","Num","M","A2"]
[null,null,"循环周期","CyclePeriod","h","Num","M","A2"]
[null,null,"额定补水量","RatedFillingFlow ","m3/天","Num","R","A2"]
[null,null,"消毒剂种类","SterilizerType",null,"MEnum","R","D2","1. 除氮磷 2. 除氯 3. 除藻类 99. 其他 （可多选）"]
[null,null,"消毒剂投放量","SterilizerRatedFeedFlow","mg/m3","Num","R","A2"]
[null,null,"消毒剂投放时间间隔","SterilizerFeedInterval","h","Num","R","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"水泵","水泵类型","PumpType",null,"Enum","R","D1","1. 离心泵 2. 柱塞泵 3. 射流泵 4. 螺杆泵 99. 其他"]
[null,null,"额定频率","PumpRatedFreq","Hz","Num","R","A2"]
[null,null,"额定扬程","PumpRatedHead","m","Num","S","A2"]
[null,null,"额定流量","PumpRatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","PumpRatedRPM","rpm","Num","M","A2"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","PumpMotorRatedEff","%","Num","R","A2"]
[null,null,"水泵额定效率","PumpRatedEff","%","Num","R","A2"]
[null,null,"特性曲线","PumpCharacterCurve",null,"Attachment","R","F1"]
[null,"过滤器","过滤介质","FilterMediumType",null,"Enum","R","D1","1. 永久性（石英砂） 2. 半永久性（聚脂纤维过滤芯、活性炭、浮石） 3. 短期（硅藻土） 99. 其他"]
[null,null,"设计滤速","FilterDesignV","m/s","Num","R","A2"]
[null,null,"滤层数","FilterLayerNum","层","Num","R","A2"]
[null,null,"滤层充填高度","FilterLayerHeight","mm","Num","R","A2"]
[null,null,"理论出水浊度","FilterRatedOutTurbidity","mg/L","Num","R","A2"]
[null,null,"理论过滤效率","FilterRatedEff","%","Num","R","A2"]
[null,null,"水反洗强度","FilterBackwashIntensity","L/s","Num","R","A2"]
[null,null,"反洗间隔","FilterBackwashInterval","h","Num","R","A2"]
[null,null,"反洗时间","FilterBackwashTime","min","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,null,null,"L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"处理水流量","WaterTreatFlow","m3/h","Inst","M","L"]
[null,null,"进口水压","WaterInPress","MPa","Inst","M","L"]
[null,null,"进口水温","WaterInTemp","℃","Inst","R","L"]
[null,null,"出口水压","WaterOutPress","MPa","Inst","M","L"]
[null,null,"出口水温","WaterOutTemp","℃","Inst","R","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","R","L"]
[null,"瞬时指标","过滤效率","FiltEff","%","Inst","R","M"]
[null,"累计指标","累计循环水量","AccCycleVolume","m3","Acc","R","M"]
[null,null,"累计补水量","AccFillingVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
["故障状态"]

{"sheet":"WSSN水景喷头","index":1,"n_rows":30,"n_cols":10,"rows_kept":30,"cut":false,"hidden":false,"merged":[[0,0,0,9],[28,0,28,1],[29,0,29,1],[13,0,27,0],[1,0,1,1],[13,1,23,1],[24,1,27,1],[2,0,12,1]]}
["喷头"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"功能类型","FuncType",null,"Enum","S","D1","1. 喷灌喷头 2. 水景喷头 99. 其他"]
[null,null,"喷头类型","NozzleType",null,"Enum","M","D1","1. 庭院喷头 2. 地埋式喷头 3. 摇臂式喷头 99. 其他","喷灌喷头"]
[null,null,"喷洒方式","SprayType",null,"Enum","R","D1","1. 散射 2. 射线 3. 旋转 4. 射线旋转 99. 其他","喷灌喷头"]
[null,null,"喷射形状","ShapeType",null,"Enum","R","D1","1. 万向直流 2. 旋转 3. 凤尾 4. 集束 5. 礼花 6. 半球 7. 环形 8. 扇形 9. 蒲公英 10. 半蒲公英 11. 玉柱 12. 雪松 13. 涌泉 14. 水雾 99. 其它","水景喷头"]
[null,null,"喷嘴直径","NozzleDiameter","mm","Num","M","A2"]
[null,null,"额定出水量","RatedWaterOutFlow","m3/h","Num","M","A2"]
[null,null,"额定出水流速","RatedWaterOutV","m/s","Num","M","A2"]
[null,null,"额定射程","RatedSprayRange","m","Num","R","A2"]
[null,null,"理论压损","RatedPressLoss","MPa","Num","R","A2"]
[null,null,"喷洒扇形角度","MaxSprayAngle","°","Num","R","A2"]
[null,null,"喷嘴材质","NozzleMaterial",null,"Enum","R","D1","1. 黄铜 2. 不锈钢 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"出水流量","WaterOutFlow","m3/h","Inst","R","L"]
[null,null,"出口流速","WaterOutV","m/s","Inst","R","L"]
[null,null,"出水压力","WaterOutPress","MPa","Inst","R","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","R","L"]
[null,null,"射程","SprayRange","m","Inst","R","M"]
[null,null,"阀门开度","ValveOpening","%","Inst","M","L"]
[null,"累计指标","累计出水量","AccSprayVolume","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","R","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"WSCU水景控制箱","index":2,"n_rows":61,"n_cols":10,"rows_kept":61,"cut":false,"hidden":false,"merged":[[60,0,60,1],[1,0,1,1],[18,1,48,1],[49,1,53,1],[0,0,0,9],[2,0,48,0],[49,0,58,0],[54,1,58,1],[59,0,59,1],[2,1,17,1]]}
["控制箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","整机","额定输入电压","RatedInputU","V","Num","R","A2"]
[null,null,"额定输出电压","RatedOutputU","V","Num","R","A2"]
[null,null,"应答时间","ResponseTime","ms","Num","M","A2"]
[null,null,"允许瞬时断电时间","AllowPowerOffTime ","ms","Num","M","A2"]
[null,null,"是否有网络功能","isNetwork",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"IP地址","IPAddress",null,"Str","S","B1"]
[null,null,"子网掩码","SubnetMask",null,"Str","S","B1"]
[null,null,"网关","Gateway",null,"Str","S","B1"]
[null,null,"DNS服务器地址","DNS",null,"Str","S","B1"]
[null,null,"适用网络类型","NetType",null,"Enum","M","D1","1. 千兆以太网 2. 万兆以太网 3. 光纤 99. 其他"]
[null,null,"传输速率","TransferSpeed","MB/s","Num","M","A2"]
[null,null,"主芯片类型","MainChip",null,"Str","R","B1"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange ","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,"接口","输入485接口数量","In485PortNum","个","Num","R","A2"]
[null,null,"输出485接口数量","Out485PortNum","个","Num","R","A2"]
[null,null,"输入232接口数量","In232PortNum","个","Num","R","A2"]
[null,null,"输出232接口数量","Out232PortNum","个","Num","R","A2"]
[null,null,"输入422接口数量","In422PortNum","个","Num","R","A2"]
[null,null,"输出422接口数量","Out422PortNum","个","Num","R","A2"]
[null,null,"输入MBUS接口数量","InMBUSPortNum","个","Num","R","A2"]
[null,null,"输出MBUS接口数量","OutMBUSPortNum","个","Num","R","A2"]
[null,null,"输入音频接口数量","InAudioPortNum","个","Num","R","A2"]
[null,null,"输出音频接口数量","OutAudioPortNum","个","Num","R","A2"]
[null,null,"HDMI接口数量","HDMIPortNum","个","Num","R","A2"]
[null,null,"VGA接口数量","VGAPortNum","个","Num","R","A2"]
[null,null,"USB接口数量","USBPortNum","个","Num","R","A2"]
[null,null,"以太网接口数量","EthernetPortNum ","个","Num","R","A2"]
[null,null,"光纤接口数量","FiberPortNum ","个","Num","R","A2"]
[null,null,"电压AI接口数量","AIUPortNum","个","Num","R","A2"]
[null,null,"电压AI信号","AIU","V","Num","R","A2"]
[null,null,"电流AI接口数量","AIIPortNum","个","Num","R","A2"]
[null,null,"电流AI信号","AII","A","Num","R","A2"]
[null,null,"电压AO接口数量","AOUPortNum","个","Num","R","A2"]
[null,null,"电压AO信号","AOU","V","Num","R","A2"]
[null,null,"电流AO接口数量","AOIPortNum","个","Num","R","A2"]
[null,null,"电流AO信号","AOI","A","Num","R","A2"]
[null,null,"DI干节点接口数量","DIDryNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点接口数量","DIWetNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点电压","DIWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"DO干节点接口数量","DODryNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点接口数量","DOWetNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点电压","DOWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"输入同轴线接口数量","InCoaxialPortNum","个","Num","R","A2"]
[null,null,"输出同轴线接口数量","OutCoaxialPortNum","个","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"在线状态","OnlineStatus",null,"Boolv","S","L","0. 脱线 1. 在线"]
[null,null,"上传速度","UploadSpeed","MB/s","Inst","R","L"]
[null,null,"下载速度","DownloadSpeed","MB/s","Inst","R","L"]
[null,"累计指标","累计上传数据量","AccUploadData","GB","Acc","R","L"]
[null,null,"累计下载数据量","AccDownloadData","GB","Acc","R","L"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","L"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","L"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"WSLT水景灯具","index":3,"n_rows":37,"n_cols":10,"rows_kept":37,"cut":false,"hidden":false,"merged":[[36,0,36,1],[1,0,1,1],[0,0,0,9],[20,0,34,0],[20,1,30,1],[31,1,34,1],[35,0,35,1],[2,0,19,1]]}
["灯具"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"灯具类型","LampType",null,"Enum","M","D1","1. 日光灯 2. LED灯 3. 白炽灯 4. 卤素灯 5. 高压气体灯 99. 其他"]
[null,null,"灯具功能","LampFuncType",null,"Enum","S","D1","1. 室内公区照明 2. 车库照明 3. 泛光照明 4. 景观照明 5. 广告照明 6. 应急照明 99. 其他"]
[null,null,"是否有自动控制","isAutoCtrl",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"照明调节类型","AdjustType",null,"Enum","M","D1","1. 通断 2. 档位 3. 连续 99. 其他"]
[null,null,"安装方式","InstallType",null,"Enum","R","D1","1. 嵌顶灯 2. 吸顶灯 3. 吊灯 4. 壁灯 5. 活动灯具 6. 外景照明 99. 其他"]
[null,null,"配光方式","LightType",null,"Enum","R","D1","1. 直接照明型 2. 半直接照明型 3. 全漫射式照明型 4. 间接照明型 99. 其他"]
[null,null,"显色指数","CRI",null,"Num","R","A1"]
[null,null,"光通量","RatedLm","lm","Num","R","A2"]
[null,null,"发光效率","RatedLmEff","%","Num","R","A2"]
[null,null,"光束角","BeamAngle","°","Num","R","A2",null,"一般常见的有10°、24°、38°三种"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"灯的档位","LampGear",null,"Enumv","M","L","1. 低档 2. 中挡 3. 高挡 99. 其他"]
[null,null,"灯的开度","LampOpening","%","Inst","M","L"]
[null,null,"光型序号","BeamID",null,"Strv","R","L"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"WSPP水景水泵","index":4,"n_rows":77,"n_cols":10,"rows_kept":77,"cut":false,"hidden":false,"merged":[[73,0,75,1],[76,0,76,1],[0,0,0,9],[1,0,1,1],[2,0,40,0],[2,1,36,1],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[67,1,72,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息"]