{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["WPCF泳池循环过滤机组"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"WPCF泳池循环过滤机组","index":0,"n_rows":96,"n_cols":10,"rows_kept":96,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[23,1,31,1],[32,1,40,1],[2,0,57,0],[45,1,47,1],[41,1,44,1],[48,1,50,1],[2,1,22,1],[86,1,91,1],[95,0,95,1],[92,0,94,1],[51,1,57,1],[58,1,77,1],[83,1,85,1],[58,0,91,0],[78,1,82,1]]}
["泳池循环过滤机组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"机组额定总功率","RatedP","kW","Num","S","A2"]
[null,null,"额定循环流量","RatedWaterCycleFlow","m3/h","Num","S","A2"]
[null,null,"机组进口管径","WaterInPipeDiameter","mm","Num","R","A2"]
[null,null,"机组出口管径","WaterOutPipeDiameter","mm","Num","R","A2"]
[null,null,"机组排污管径","SewagePipeDiameter","mm","Num","R","A2"]
[null,null,"泳池容积","SwimPoolCap","m3","Num","M","A2"]
[null,null,"泳池水循环周期","WaterCyclePeriod","h","Num","M","A2"]
[null,null,"理论补水量","RatedFillingFlow","m3/天","Num","R","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"水泵","水泵类型","PumpType",null,"Enum","R","D1","1. 离心泵 2. 柱塞泵 3. 射流泵 4. 螺杆泵 99. 其他"]
[null,null,"水泵额定频率","PumpRatedFreq","Hz","Num","R","A2"]
[null,null,"水泵额定扬程","PumpRatedHead","m","Num","S","A2"]
[null,null,"水泵额定流量","PumpRatedFlow","m3/h","Num","S","A2"]
[null,null,"水泵额定转速","PumpRatedRPM","rpm","Num","M","A2"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"水泵电机额定效率","PumpMotorRatedEff","%","Num","R","A2"]
[null,null,"水泵额定效率","PumpRatedEff","%","Num","R","A2"]
[null,null,"水泵特性曲线","PumpCharacterCurve",null,"Attachment","R","F1"]
[null,"过滤器","过滤介质","FilterMediumType",null,"Enum","R","D1","1. 永久性（石英砂） 2. 半永久性（聚脂纤维过滤芯、活性炭、浮石） 3. 短期（硅藻土） 99. 其他"]
[null,null,"过滤器设计滤速","FilterDesignV","m/s","Num","R","A2"]
[null,null,"过滤器滤层数","FilterLayerNum","层","Num","R","A2"]
[null,null,"过滤器滤层充填高度","FilterLayerHeight","mm","Num","R","A2"]
[null,null,"过滤器理论出水浊度","FilterRatedOutTurbidity","mg/L","Num","R","A2"]
[null,null,"过滤器理论过滤效率","FilterRatedEff","%","Num","R","A2"]
[null,null,"过滤器水反洗强度","FilterBackwashStrength","L/s","Num","R","A2"]
[null,null,"过滤器反洗间隔","FilterBackwashInterval","h","Num","R","A2"]
[null,null,"过滤器洗时间","FilterBackwashTime","min","Num","R","A2"]
[null,"紫外线杀菌器","紫外线杀菌器灯管数量","UVLampNum","个","Num","R","A2"]
[null,null,"紫外线杀菌器额定强度","UVRatedIntensity","W/m2","Num","R","A2"]
[null,null,"紫外线杀菌器额定杀菌率","UVRatedSterilizeRate","%","Num","R","A2"]
[null,null,"紫外线杀菌器额定处理速率","UVRatedTreatFlow","m3/h","Num","R","A2"]
[null,"臭氧发生器","臭氧发生器额定产量","OzoneRatedGenerateFlow","mol/h","Num","R","A2"]
[null,null,"臭氧发生器额定杀菌率","OzoneRatedSterilizeRate","%","Num","R","A2"]
[null,null,"臭氧发生器额定处理速率","OzoneRatedTreatFlow","m3/h","Num","R","A2"]
[null,"消毒剂","消毒剂种类","SterilizerType",null,"Enum","R","D1","1. 消毒粉 2. 消毒片 99. 其他"]
[null,null,"消毒剂投放量","SterilizerRatedFeedFlow","mg/m3","Num","R","A2"]
[null,null,"消毒剂投放间隔时间","SterilizerFeedInterval","h","Num","R","A2",null,"可直接投放水池中，也可通过药泵投加；加完后半小时检测水质是否达标"]
[null,"加热器","加热器热源类型","HeatSourceType",null,"Enum","M","D1","1. 热源换热 2. 电加热 99. 其他"]
[null,null,"加热器额定功率","HeaterRatedP","kW","Num","M","A2"]
[null,null,"加热器额定进水温度","HeaterRatedInTemp","℃","Num","R","A2"]
[null,null,"加热器额定出水温度","HeaterRatedOutTemp","℃","Num","R","A2"]
[null,null,"加热器工作压力范围","HeaterWorkPressRange","MPa","Numr","R","A2"]
[null,null,"加热器换热面积","HeaterRatedTransArea","m2","Num","R","A2"]
[null,null,"加热器额定换热效率","HeaterRatedTransEff","%","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作总电流","I","A","Inst","M","L"]
[null,null,"机组耗电总功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"循环流量","WaterCycleFlow","m3/h","Inst","M","L"]
[null,null,"补水流量","FillingFlow","m3/h","Inst","R","L"]
[null,null,"机组进水压力","WaterInPress","MPa","Inst","S","L"]
[null,null,"机组进水温度","WaterInTemp","℃","Inst","M","L"]
[null,null,"机组出水压力","WaterOutPress","MPa","Inst","S","L"]
[null,null,"机组出水温度","WaterOutTemp","℃","Inst","M","L"]
[null,null,"泳池出水流速","SwimPoolWaterOutV","m/s","Inst","R","L"]
[null,null,"泳池进水流速","SwimPoolWaterInV","m/s","Inst","R","L"]
[null,null,"过滤器滤速","FilterV","m/s","Inst","R","L"]
[null,null,"紫外线强度","UvIntensity","W/m2","Inst","R","L"]
[null,null,"臭氧产量","OzoneGenerateFlow","mol/h","Inst","R","L"]
[null,null,"加热功率","HeatP","kW","Inst","M","L"]
[null,"出口水质","水硬度","WaterOutHardness","mg/L","Inst","R","L",null,"主要为CaCO3含量"]
[null,null,"尿素","WaterOutCarbamide","mg/L","Inst","R","L",null,"不超过3.5mg/L"]
[null,null,"浑浊度","WaterOutTurbidity","NTU","Inst","R","L"]
[null,null,"PH","WaterOutPH",null,"Inst","R","L",null,"6.5-8.5"]
[null,null,"游离性余氯","WaterOutFreeCl","mg/L","Inst","R","L",null,"游泳余氯 0.4-0.6；化合性余氯1.0以上"]
[null,"瞬时指标","过滤效率","FiltEff","%","Inst","R","M"]
[null,null,"杀菌率","SterilizeRate","%","Inst","R","M",null,"需要不定时取样检测"]
[null,null,"加热效率","HeatEff","%","Inst","R","M"]
[null,"累计指标","累计处理水量","AccWaterTreatVolume","m3","Acc","R","M"]
[null,null,"累计补水量","AccFillingVolume","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息"]