{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["List","关系定义与编码","图类型"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"List","index":0,"n_rows":35,"n_cols":13,"rows_kept":35,"cut":false,"hidden":false,"merged":[[27,5,32,5],[1,5,1,6],[2,4,4,4],[2,5,4,5],[5,2,12,2],[13,2,26,2],[5,5,12,5],[13,5,26,5],[33,1,34,1],[27,2,32,2],[2,1,32,1],[1,1,1,2],[2,2,4,2]]}
[]
[null,null,null,"关系的属性类别","关系的传递性","说明",null,"举例"]
[null,"物理世界层","架构从属关系","元空间-元空间","可传递","存在于同类不同层级的对象之间，树形结构",null,"建筑空间类对象关系树（项目-建筑体-楼层-空间）"]
[null,null,null,"设备-设备",null,null,null,"机电设备类对象关系树（项目-系统-设备-部件）"]
[null,null,null,"设施-设施",null,null,null,"土建设施类对象关系树（项目-设施-组件）"]
[null,null,"物理连接关系","元空间-元空间",null,"与BIM直接对应的关系，只考虑对象在物理层面上相连接",null,"空间之间的相邻关系（各个方向）"]
[null,null,null,"设备-设备",null,null,null,"设备之间的连接关系（如两管段连接，管段与支架连接）",{"$nulls":4}," "]
[null,null,null,"设施-设施",null,null,null,"设施之间的连接关系（如门与墙连接）"]
[null,null,null,"元空间-设备",null,null,null,"设备所在空间（如冷机在冷站机房中）"]
[null,null,null,"元空间-设施",null,null,null,"设施所在/参与构成空间（如盥洗盆在卫生间中，幕墙参与构成一系列空间）"]
[null,null,null,"设备-设施",null,null,null,"设备与设施的连接关系（如生活给水龙头与盥洗台盆连接）"]
[null,null,null,"固定的联结关系","可传递",null,"对象之间固定联结，需整体移动","（如同一建筑体内相邻空间，冷机与冷冻水供水管连接）"]
[null,null,null,"非固定的接触关系","不可传递",null,"对象之间位置上接触，可独立移动"," "]
[null,null,"介质流通关系","元空间-元空间",null,"某种特定介质可以在两个对象之间流通的关系，与物理连接关系是不同层面的关系",null,"空间流通关系（人员流通，空气流通，光照辐射）"]
[null,null,null,"设备-设备",null,null,null,"设备流通关系（冷冻水环路设备，空调送风管路设备，配电线路设备，控制线路设备）"]
[null,null,null,"元空间-设备",null,null,null,"空间与设备流通关系（空调送风到房间，消防给水到房间，房间回风到空调系统）"]
[null,null,null,"开式",null,null,"介质单向流动，在末端耗散","（如直饮水给水系统，配电系统）"]
[null,null,null,"闭式",null,null,"介质循环流动","（如冷冻水循环系统，供热系统）"]
[null,null,null,"人员",null,null,"人员可通过，空间-空间","（如人员交通网络）"]
[null,null,null,"固体",null,null,"颗粒状固体可流通","（如锅炉送煤设备）"]
[null,null,null,"液体",null,null,"液体可流通","（如生活给水系统）"]
[null,null,null,"气体",null,null,"气体可流通","（如消防排烟系统）"]
[null,null,null,"强电",null,null,"强电电流可流通","（如配电系统）"]
[null,null,null,"弱电",null,null,"弱电信号可流通","（如网络系统）"]
[null,null,null,"电磁波辐射",null,null,"电磁波可传播","（如光、辐射、wifi等）"]
[null,null,null,"有组织",null,null,"由机械系统或管道组织","（如空调送风系统）"]
[null,null,null,"无组织",null,null,"介质的自然流通","（如空间之间的自然通风）"]
[null,null,"抽象关联关系","元空间-元空间",null,"与某种功能有关而形成的对象之间的关系，与物理上的连接和流通关系都是不同层面上的关系",null,"（如机房与其服务的空间）"]
[null,null,null,"设备-设备",null,null,null,"（如配电关系、受控关系）"]
[null,null,null,"设施-设施",null,null,null,"（如承重分配关系）"]
[null,null,null,"元空间-设备",null,null,null,"设备与服务空间的关系"]
[null,null,null,"元空间-设施",null,null,null,"（如遮阳帘与被遮阳空间的关系）"]
[null,null,null,"设备-设施",null,null,null,"（如外景射灯与外墙的关系）"]
[null,"虚拟应用层","功能上的关联关系",null,null,"有物理世界之外的对象参与的与某种功能实现相关而产生的关系",null,"（如租户与空间关系、能耗分项与设备关系、自控系统与弱电线路关系）"]
[null,null,"管理上的关联关系",null,null,"有物理世界之外的对象参与的与组织管理方式相关而产生的关系",null,"（如采购投产关系）"]

{"sheet":"关系定义与编码","index":1,"n_rows":64,"n_cols":8,"rows_kept":64,"cut":false,"hidden":false,"merged":[[58,1,59,1],[58,2,59,2],[58,6,59,6],[54,1,55,1],[54,2,55,2],[54,6,55,6],[56,1,57,1],[56,2,57,2],[56,6,57,6],[50,1,51,1],[50,2,51,2],[50,6,51,6],[52,1,53,1],[52,2,53,2],[52,6,53,6],[46,1,47,1],[46,2,47,2],[46,6,47,6],[48,1,49,1],[48,2,49,2],[48,6,49,6],[39,1,40,1],[39,2,40,2],[39,6,40,6],[42,1,44,1],[42,2,44,2],[42,6,44,6],[24,7,25,7],[26,1,29,1],[26,2,29,2],[26,6,29,6],[35,1,38,1],[35,2,38,2],[35,6,38,6],[30,1,33,1],[30,2,33,2],[30,6,33,6],[20,1,21,1],[20,2,21,2],[22,1,23,1],[22,2,23,2],[24,1,25,1],[24,2,25,2],[24,6,25,6],[13,1,14,1],[13,2,14,2],[13,6,14,6],[15,1,16,1],[15,2,16,2],[15,6,16,6],[10,1,12,1],[10,2,12,2],[10,6,12,6],[3,1,4,1],[3,2,4,2],[5,1,9,1],[5,2,9,2],[5,6,9,6]]}
[]
[null,"关系类型","关系名称","边类型","边名称","边方向","主要连接对象","逻辑概述"]
[null,"ElementSpinFloor","元空间所在楼层",1,"位于",1,"楼层→元空间","此处空间为元空间"]
[null,"EquipinFloor","设备所在楼层",1,"位于",1,"楼层→设备","此处的设备包括设备和部件"]
[null,null,null,0,"不确定",0,"楼层-设备","此处的设备包括设备和部件"]
[null,"ElementSpNeighborhood","空间邻接关系",1,"隔断无门窗",0,"元空间-元空间","几何邻接，由墙、幕墙、楼板、玻璃隔断分隔"]
[null,null,null,2,"隔断有门",0,null,"几何邻接，有门"]
[null,null,null,3,"隔断有窗",0,null,"几何邻接，有窗"]
[null,null,null,4,"隔断有门窗",0,null,"几何邻接，有门和窗"]
[null,null,null,5,"连通",0,null,"几何邻接，无完整分隔"]
[null,"TrafficNetwork","建筑交通网络",1,"普通",0,"元空间-元空间","空间邻接关系-2,4,5"]
[null,null,null,2,"消防常开",0,null,"空间邻接关系-2,4，且消防常开门"]
[null,null,null,3,"消防常关",0,null,"空间邻接关系-2,4，且消防常关门"]
[null,"ConvectionNetwork","空气流通网络",1,"自然对流",0,"元空间-元空间"]
[null,null,null,2,"机械通风",1]
[null,"RadiationNetwork","光照辐射网络",1,"连通",0,"元空间-元空间"]
[null,null,null,2,"透明隔断",0]
[null,"EquipinElementSp","设备所在空间",1,"位于",1,"元空间→设备","此处的设备包括设备和部件"]
[null,"EquipforElementSp","设备服务空间",1,"服务于",1,"设备→元空间","此处的设备包括设备和部件"]
[null,"SystemEquip","系统包含的设备",1,"包括",1,"系统→设备","此处的设备包括设备和部件"]
[null,"LUDistribution","低压配电系统",1,"普通连接",1,"变压器-TDTF;低压开关柜-TDLS","变压器→低压开关柜（进线柜）\n低压开关柜→低压开关柜"]
[null,null,null,2,"互备连接",0,"低压开关柜-TDLS","低压开关柜（进线柜）- 低压开关柜（母联柜）"]
[null,"HUDistribution","高压变配电系统",1,"普通连接",0,"变压器-TDTF;高压开关柜-TDHS;直流屏-TDDS","高压开关柜 - 变压器\n高压开关柜 - 高压开关柜\n高压开关柜 - 直流屏"]
[null,null,null,2,"互备连接",0,"高压开关柜-TDHS","高压开关柜 - 分段主柜\n高压开关柜 - 分段辅柜"]
[null,"EquipPower","设备电源",1,"常规",1,"低压开关柜→设备","设备暂时认为是所有设备和部件"]
[null,null,null,2,"备用",1]
[null,"ChillWaterLoop","空调冷冻水环路",1,"供水",1,"离心式冷水机组-CCCC;螺杆式冷水机组-CCSC;吸收式冷水机组-CCAC;空气源热泵-CCAH;水源热泵-CCWH;地源热泵-CCGH;供冷冷冻水泵-CCCP;供冷补水泵-CCFP;供冷定压补水装置-CCCF;供冷换热器-CCHE;供冷分水器-CCDB;供冷集水器-CCCL;空调机组-ATAH;新风机组-ATFU;风机盘管-ATFC;散热器-ATRD"]
[null,null,null,2,"回水",1]
[null,null,null,3,"旁通",0]
[null,null,null,4,"补水",1]
[null,"CoolingWaterLoop","空调冷却水环路",1,"供水",1,"离心式冷水机组-CCCC;螺杆式冷水机组-CCSC;吸收式冷水机组-CCAC;地源热泵-CCGH;冷却塔-CCOT;供冷冷却水泵-CCOP;地埋管-CCGHBP"]
[null,null,null,2,"回水",1]
[null,null,null,3,"旁通",0]
[null,null,null,4,"补水",1]
[null,"CondWaterNetwork","空调冷凝水网络",1,"排水",1,"空调机组-ATAH;新风机组-ATFU;风机盘管-ATFC;"]
[null,"HeatWaterLoop","采暖水环路",1,"供水",1,"供热燃煤锅炉-CHCB;供热燃油锅炉-CHFB;供热燃气锅炉-CHGB;供热电锅炉-CHEB;供热水泵-CHHP;供热补水泵-CHFP;供热定压补水装置-CHCF;供热换热器-CHHE;供热分水器-CHDB;供热集水器-CHCL;空调机组-ATAH;新风机组-ATFU;风机盘管-ATFC;地板空调器-ATFA;散热器-ATRD;地板采暖设备-ATFH"]
[null,null,null,2,"回水",1]
[null,null,null,3,"旁通",0]
[null,null,null,4,"补水",1]
[null,"ACAirNetwork","空调风管网",1,"送风",1,"空调机组-ATAH;风机盘管-ATFC;VAVBOX-ATVA;空调风口-ATIO"]
[null,null,null,2,"回风",1]
[null,"FreshAirNetwork","新风管网",1,"送风",1,"新风机组-ATFU;空调风口-ATIO"]
[null,"VentNetwork","通风管网",1,"送风",1,"通风风机-VTSF;通风风口-VTIO;厨房风机-KLSF;厨房风口-KLIO;人防风机-ADSF;人防风口-ADIO"]
[null,null,null,2,"排风",1]
[null,null,null,3,"不确定",0]
[null,"VRFNetwork","多联机系统",1,"供制冷剂",1,"多联机室外机-ATVO → 多联机室内机-ATVI"]
[null,"SupplyWaterNetwork","给水网络",1,"给水",1,"生活给水供水机组-DWSU;生活给水储水箱-DWWT"]
[null,null,null,2,"旁通",0]
[null,"DrainingWaterNetwork","排水网络",1,"排水",1,"污废水一体式提升机组-STLU;潜污泵-STSP;化粪池-STST;集水坑-STCP"]
[null,null,null,2,"旁通",0]
[null,"RecycleWaterNetwork","中水系统",1,"排水",1,"中水供水机组-RWSU;中水处理机组-RWTU;中水储水箱-RWWT;雨水收集设备-RWRC"]
[null,null,null,2,"旁通",0]
[null,"DrinkingWaterNetwork","直饮水网络",1,"直饮水",1,"直饮水处理机组-DDTU;即时加热器-DDIH"]
[null,null,null,2,"旁通",0]
[null,"DHWNetwork","生活热水网络",1,"供热水",1,"生活热水燃煤锅炉-DHCB;生活热水燃油锅炉-DHFB;生活热水燃气锅炉-DHGB;生活热水电锅炉-DHEB;生活热水燃气热水器-DHGH;生活热水电热水器-DHEH;生活热水太阳能集热器-DHSC;生活热水辅热设备-DHHA;生活热水换热器-DHHE;生活热水水泵-DHHP;生活热水储水箱-DHWT;生活热水空气源热泵-DHAH"]
[null,null,null,2,"旁通",0]
[null,"GasNetwork","燃气系统",1,"供气",1,"燃气调压箱-FGPA;液化石油气瓶-FGLP"]
[null,null,null,2,"旁通",0]
[null,"FireWaterNetwork","消防供水网络",1,"供水",1,"消火栓供水加压泵-FSHP;喷淋供水加压泵-FSSP;水喷雾供水加压泵-FSMP;停机坪消防供水加压泵-FSAP;消防水炮设备-FSWM;消防稳压设备-FSPS;消火栓箱-FSHB;室外消火栓-FSOH;末端试水装置-FSET"]
[null,null,null,2,"旁通",0]
[null,"FireVentNetwork","消防排烟网络",1,"排风",1,"防排烟风机-SCEF;排烟风口-SCIO;防火排烟阀-SCSD"]
[null,"SensorNetwork","传感器通信网络",1,"连接",1,"温度传感器-SETP;湿度传感器-SERH;压力传感器-SEPS;浓度传感器-SECT;速度传感器-SESP;位移传感器-SEDP;流量传感器-SEFL;热量传感器-SEHT;电度传感器-SEEE;声音传感器-SESD;图像传感器-SEVD;人流量传感器-SEPF;组合式传感器-SECB"]
[null,"ControlEquipNetwork","控制设备网络",1,"连接",1,"楼控主机-BAHT;楼控控制箱-BACU;楼控控制面板-BACP"]
[null,"ControlRelation","对象受控关系",1,"连接",1,"楼控控制面板-BACP → 设备\n楼控网络控制器-BANC → 设备","此处的设备包括设备和部件"]

{"sheet":"图类型","index":2,"n_rows":17,"n_cols":4,"rows_kept":17,"cut":false,"hidden":false,"merged":[]}
["名称","图类型","关系类型","备注"]
["资产和建筑关系","PE2Bd",1,"资产id->建筑id"]
["资产和楼层关系","PE2Fl",1,"资产id->楼层id"]
["资产和岗位","PE2Eq",1,"资产id->设备或部件id"]
["建筑和楼层关系","Bd2Fl",1]
["建筑和空间","Bd2Sp",1]
["建筑和系统","Bd2Sy",1]
["建筑和设备、部件","Bd2Eq",1]
["楼层和空间","Fl2Sp",1]
["设备和部件","Eq2Ec",1]
["用电分项能耗模型","SubE",1,"VOSe-VOSe"]
["用冷分项能耗模型","SubC",1,"VOSc-VOSc"]
["用热分项能耗模型","SubH",1,"VOSh-VOSh"]
["用水分项能耗模型","SubW",1,"VOSw-VOSw"]
["用燃气分项能耗模型","SubG",1,"VOSg-VOSg"]
["用燃油分项能耗模型","SubF",1,"VOSf-VOSf"]
["用蒸汽分项能耗模型","SubV",1,"VOSv-VOSv"]